## BOQ
BILL OF QUANTITY
Name of work:- SITC of 1 x 4.5 TR Tower type & 3 x 2.0 TR Hi-wall mounted FCU's i/c P/F MS pipe, Valve etc. & associated works on VLSI Course lab and Server room at 1st floor WL-211A.
Name of agency:-
S.No. | Description | Qty | Unit | Rate | Amount
1 | SITC of Fan Coil Unit (Hi-Wall mounted), The unit shall be complete with insulated enclosure, comprising of blower, 2/3 speed motor with fan speed controller, 2/3 row copper coil section, washable filter section, 2 way motorized valve with actuator, remote controller and brass flair fitting for copper pipe connection, i/c all necessary support /hangers, vibration isolators etc. complete as reqd.
a) | 2.0 TR nominal or higher capacity | 3 | No. |  | 0
2 | SITC of Fan Coil Unit (Tower type), The unit shall be complete with insulated enclosure, comprising of blower, 2/3 speed motor with fan speed controller, 2/3 row copper coil section, washable filter section, 2 way motorized valve with actuator, remote controller and brass flair fitting for copper pipe connection, i/c all necessary support , wooden stand, vibration isolators etc. complete as reqd.
a) | 4.5 TR nominal or higher capacity | 1 | No. |  | 0
3 | Providing, fixing, testing & commissioning of 2-way Motorized valve with actuator in fan coil units of following Capacity including dismantling of old if any etc. complete as reqd.
a) | Up to 2.0 TR Capacity | 1 | Nos |  | 0
4 | Providing & fixing of brass ball valve with Y-strainer of following size with compatible to proportioning Copper/MS pipe i/c all necessary support /hangers & dismantling old if any complete as reqd.
a) | 25 mm | 4 | Nos |  | 0
5 | Providing & fixing of SS ball valve of following size with compatible to proportioning Copper/MS pipe i/c all necessary accessories, support /hangers, including old dismantling if any complete as reqd.
a) | 20 mm | 4 | Nos |  | 0
b) | 25 mm | 3 | Nos |  | 0
6 | Providing & fixing in position the mercury in glass industrial type thermometers. | 2 | Nos |  | 0
7 | Providing and fixing in position the 0-150 PSIG industrial type pressure gauges with gun metal / brass petcock valves & MS nipple, socket etc complete as required | 2 | Nos |  | 0
8 | Providing & fixing of Brass Air-Vent of following size with compatibleCopper/MS pipe i/c all necessary accessories & dismantling old if any complete as reqd.
a) | 20 mm dia | 2 | Nos |  | 0
b) | 25 mm dia | 2 | Nos |  | 0
9 | SITC of Butterfly valves CI body with SS Disc Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water with hand lever operated including nut, bolt, flanges, gasket and insulation of valve as kind of existing pipe etc. complete as reqd.
a) | 40 mm | 4 | Nos |  | 0
10 | Supply, laying /fixing, testing and commissioning of MS Heavy 'C' class pipe ( IS :1239) of following sizes for chilled/ condenser water piping on surface / underground ( including fabrication of bends / elbows, tees, reducers, sockets, unions etc) with wooden / PUf block, masonry support / MS angle-clamp two coats primer/ enamel paint, vibration isolatorsand fittings as per standard specification complete as required.
a) | 25 mm | 24 | Mtr |  | 0
b) | 32 mm | 30 | Mtr |  | 0
c) | 40 mm | 14 | Mtr |  | 0
11 | Supplying & fixing insulation on existing MS 'C' class pipe over exposed surface/underground of following sizes with 50 mm thick fire retardant thermocole ( polystrene) moulded pipe section of density 20 kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessain cloth, wiremesh, sand-cement plaster & enamel painting two or more coat to give even shade after applying one coat of ordinary paint etc complete as required.
a) | 25 mm | 20 | Mtr |  | 0
a) | 32 mm | 30 | Mtr |  | 0
b) | 40 mm | 14 | Mtr |  | 0
a) | 50 mm | 1 | Mtr |  | 0
b) | 65 mm | 1 | Mtr |  | 0
c) | 80 mm | 1 | Mtr |  | 0
12 | Providing & fixing of thermal insulation with aluminium foil faced expended polyethylene foam (XLPE) Class 'O' insulation sheet of following thickness on existing surface of pipe/duct with dentrite/adhesive etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminum tape complete as required. As per specification.
a) | 6 mm | 6 | Sqm |  | 0
b) | 13 mm | 4 | Sqm |  | 0
13 | Providing and fixing Aluminium cladding made of 26 swg thick aluminium sheet i/c bend, reducer, tee, cap end etc complete as required. | 20 | Sqm |  | 0
14 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge.(Internal work - Exposed on wall)
a) | 20 mm nominal outer dia Pipes | 20 | Mtr |  | 0
b) | 25 mm nominal outer dia Pipes | 20 | Mtr |  | 0
15 | Providing, laying, testing, and commissioning of following size Un-armoured PVC insulated Copper conducter power/controle cable of following size on surface/recessed complete as required.
a) | 3 Core x 1.5 Sqmm, flexible Un-armoured copper cable | 18 | Mtr |  | 0
16 | Providing and fixing of Single Phase Plug top ISI Marked for AC (FCU) unit etc i/c dismentling old plug top if any complete as required. (Make:- Anchor or Equvilant)
a) | 3 pin- 6 Amp. | 4 | Nos |  | 0
17 | Providing,laying & fixing of rainforced fiber flexible/soft PVC pipe of size given below etc. complete as reqd.
a) | 20 mm | 3 | Mtr |  | 0
b) | 25 mm | 2 | Mtr |  | 0
18 | Supply & fixing of copper piping 5/8" or 6/8" with 19 mm thick Class "O" Nitrile insulation on surface / recessed with flair nut, clamps etc. complete as reqd. | 8 | Mtr |  | 0
19 | Cutting & dismantling of damaged and defective insulation, removing the thermocole , nitrile, PUF insulation or clading from chilled water MS pipe line of size mentioned below including hessian cloth, wire mesh, sand, cement, plaster, cleaning of pipe and shifting the waste material within the permises of I.I.T. K. campus or desired location as reqd.
a) | 20 mm to 100 mm dia. | 6 | Mtr |  | 0
20 | Cutting & Dismantling of condensor / chilled water pipe line of following size for drain out the water from supply & return pipe line and making good i/c re-filling of water in pipe line ,testing & commissioning complete as required.
a) | 20 mm to 100 mm dia | 1 | Job |  | 0
21 | Providing & fixing of Thermal protecting layer (double coat ) painting over exposed MS/copper pipe insulation outer surface with aapproved make chemical, shade and glass clothc as per standared specification compete as required.
a) | 20 mm | 10 | Mtr |  | 0
b) | 25 mm | 12 | Mtr |  | 0
c) | 32 mm | 6 | Mtr |  | 0
22 | Making wall opening upto 600mm dia in any type / thick of wall and re-closing the opening with brick, sand, cement and plaster upto 20 mm i/c re-painting as per existing desigine/shape complete as required. | 5 | Nos |  | 0
| Total |  |  |  | 0