## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: SITC of 38 HP Inverter variable refrigerant flow (IVRF) type AC System and associated work at SL-212.
NIT No: HVAC/22/08/2023-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Component | [53 empty] | 1 | Component
1.01 | Part (A) High Side Works (Equipment & accessories) | item no.1 | [52 empty] | 1.01 | Part (A) High Side Works (Equipment & accessories) | item no.1
1.02 | Variable Refrigerant Flow/Variable Refrigerant Volume System | item no.2 | [52 empty] | 1.02 | Variable Refrigerant Flow/Variable Refrigerant Volume System | item no.2
1.03 | Outdoor Unit (IVRV/IVRF) | item no.3 | [52 empty] | 1.03 | Outdoor Unit (IVRV/IVRF) | item no.3
1.04 | Supply, installation, testing and commissioning of following modular type Variable Refrigerant Flow / Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed 100% inverter all Scroll Compressor(s), minimum two compressors for above 14 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R-410A Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V+/-10%, 3Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. | item no.4 | [52 empty] | 1.04 | Supply, installation, testing and commissioning of following modular type Variable Refrigerant Flow / Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed 100% inverter all Scroll Compressor(s), minimum two compressors for above 14 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R-410A Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V+/-10%, 3Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. | item no.4
1.05 | 20 HP or higher capacity | item no.5 | 1 | No. | 505000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 505000 | 505000 | INR Five Lakh Five Thousand Only | 1.05 | 20 HP or higher capacity | item no.5 | 1 | No.
1.06 | 18 HP or higher capacity | item no.6 | 1 | No. | 461000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 461000 | 461000 | INR Four Lakh Sixty One Thousand Only | 1.06 | 18 HP or higher capacity | item no.6 | 1 | No.
1.07 | Indoor Unit (Ductable) | item no.7 | [52 empty] | 1.07 | Indoor Unit (Ductable) | item no.7
1.08 | Supply, installation, testing and commissioning of following minimum capacity and external static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration isolators, drain pan, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The unit shall have automatic force shut down provision in case of fire on receiveing signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | item no.8 | [52 empty] | 1.08 | Supply, installation, testing and commissioning of following minimum capacity and external static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration isolators, drain pan, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The unit shall have automatic force shut down provision in case of fire on receiveing signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | item no.8
1.09 | High Static Ductable units (min. 110 pascal external SP/Heigher) | item no.9 | [52 empty] | 1.09 | High Static Ductable units (min. 110 pascal external SP/Heigher) | item no.9
1.1 | 5.5 TR or higher capacity | item no.10 | 2 | Nos. | 78950 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 157900 | 157900 | INR One Lakh Fifty Seven Thousand Nine Hundred Only | 1.1 | 5.5 TR or higher capacity | item no.10 | 2 | Nos.
1.11 | 7.0 TR or higher capacity | item no.11 | 1 | No. | 83500 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 83500 | 83500 | INR Eighty Three Thousand Five Hundred Only | 1.11 | 7.0 TR or higher capacity | item no.11 | 1 | No.
1.12 | Indoor Unit (4-Way Cassette) | item no.12 | [52 empty] | 1.12 | Indoor Unit (4-Way Cassette) | item no.12
1.13 | Supply, installation, testing and commissioning of following minimum capacity 4-way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve,outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature | item no.13 | [52 empty] | 1.13 | Supply, installation, testing and commissioning of following minimum capacity 4-way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve,outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature | item no.13
1.14 | 2.0 TR or higher capacity … | item no.14 | 5 | Nos. | 54300 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 271500 | 271500 | INR Two Lakh Seventy One Thousand Five Hundred Only | 1.14 | 2.0 TR or higher capacity … | item no.14 | 5 | Nos.
1.15 | Floor Mounted DX-AHU (VRF compatible with HEPA Filter) | item no.15 | [52 empty] | 1.15 | Floor Mounted DX-AHU (VRF compatible with HEPA Filter) | item no.15
1.16 | Supply, installation, testing and commissioning of following Floor Mounted, Double Skin AHU with Mixing Chamber, fan-section with Forward curved centrifugal fan/blower on anti-vibration spring mounts or cushyfoot mount. Framework shall be thermal break aluminum profile, panels pre plasticized/ coated G.I. casing 0.6 mm thick outside and 0.6 mm thick inside with 46/50 mm injected PUF of density 40+2 kg/cuM. fire retardent flexible connection, Mixing box section shall be equipped with opposed action Aluminium dampers of various sizes for supply air & return air. double sloping SS drain pan with 13 mm nitrile/XLPE insulation, coil section with 6/4 Rows DX copper coil, electronic expansion valve with EEV Kit, having limit Switch, LED light i/c control wiring. VFD compatible variable speed squirrel cage induction TEFC efficiency IE-03 motor with IP-54 protection. Motor shall be suitable for 415±10% volts, 50 Hz, 3 phase AC supply. Box type Filter-section with washable pre-filter (MERV-8) with fine filter (MERV-13). AHU shall be selected for maximum face velocity of 500 FPM (2.5 MPS) and Fan outlet velocity shall not exceed 2000 FPM (10.1 MPS). | item no.16 | [52 empty] | 1.16 | Supply, installation, testing and commissioning of following Floor Mounted, Double Skin AHU with Mixing Chamber, fan-section with Forward curved centrifugal fan/blower on anti-vibration spring mounts or cushyfoot mount. Framework shall be thermal break aluminum profile, panels pre plasticized/ coated G.I. casing 0.6 mm thick outside and 0.6 mm thick inside with 46/50 mm injected PUF of density 40+2 kg/cuM. fire retardent flexible connection, Mixing box section shall be equipped with opposed action Aluminium dampers of various sizes for supply air & return air. double sloping SS drain pan with 13 mm nitrile/XLPE insulation, coil section with 6/4 Rows DX copper coil, electronic expansion valve with EEV Kit, having limit Switch, LED light i/c control wiring. VFD compatible variable speed squirrel cage induction TEFC efficiency IE-03 motor with IP-54 protection. Motor shall be suitable for 415±10% volts, 50 Hz, 3 phase AC supply. Box type Filter-section with washable pre-filter (MERV-8) with fine filter (MERV-13). AHU shall be selected for maximum face velocity of 500 FPM (2.5 MPS) and Fan outlet velocity shall not exceed 2000 FPM (10.1 MPS). | item no.16
1.17 | 5.0 TR, 2000 cfm, 110-120 mm SP or higher capacity. | item no.17 | 1 | No. | 200000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 200000 | 200000 | INR Two Lakh Only | 1.17 | 5.0 TR, 2000 cfm, 110-120 mm SP or higher capacity. | item no.17 | 1 | No.
1.18 | Supply, installation, testing and commissioning of communication Kit with corded remote control i/c control wiring for specified AHU compatible to DX type VRF unit complete as required | item no.18 | 1 | Set | 33300 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 33300 | 33300 | INR Thirty Three Thousand Three Hundred Only | 1.18 | Supply, installation, testing and commissioning of communication Kit with corded remote control i/c control wiring for specified AHU compatible to DX type VRF unit complete as required | item no.18 | 1 | Set
1.19 | Supply and fixing of low pressure loss HEPA (High Efficiency Particle Arresting) filters (MERV-17) of specified size I/c matalic frame for clean room inside/outside of as required. | item no.19 | 2 | SqM | 14500 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 29000 | 29000 | INR Twenty Nine Thousand Only | 1.19 | Supply and fixing of low pressure loss HEPA (High Efficiency Particle Arresting) filters (MERV-17) of specified size I/c matalic frame for clean room inside/outside of as required. | item no.19 | 2 | SqM
1.2 | Y-Joints & Headers | item no.20 | [52 empty] | 1.2 | Y-Joints & Headers | item no.20
1.21 | Supply, installation, testing and commissioning of following imported fittings (Refnet/Y-Joint) in Supply & return refrigerant pipe line. Material of construction for fittings shall be OEM specified and similar to refrigerant piping. | item no.21 | [52 empty] | 1.21 | Supply, installation, testing and commissioning of following imported fittings (Refnet/Y-Joint) in Supply & return refrigerant pipe line. Material of construction for fittings shall be OEM specified and similar to refrigerant piping. | item no.21
1.22 | Y- joints for IDU - IDU refrigerant piping | item no.22 | 7 | Set | 4200 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 29400 | 29400 | INR Twenty Nine Thousand Four Hundred Only | 1.22 | Y- joints for IDU - IDU refrigerant piping | item no.22 | 7 | Set
1.23 | Digital central / group conntroller | item no.23 | [52 empty] | 1.23 | Digital central / group conntroller | item no.23
1.24 | Supply, installation, testing and commissioning of following type VRF/ VRV type Digital central/ group conntroller i/c hardware, software and control/ communication cable compatible VRF (DX type) AHU, IDU's system by Original equipment manufature (OEM). The unit operation on single phase AC supply 230V±10%, 50Hz by which following minimum operations/ facility can be done for min 30 units. 1) Operation display & history, ON/Off, Mode, Temp, Fans-peed, Fault /Error display/ record, Operation group/ individual etc complete as required. | item no.24 | 1 | No. | 35000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 35000 | 35000 | INR Thirty Five Thousand Only | 1.24 | Supply, installation, testing and commissioning of following type VRF/ VRV type Digital central/ group conntroller i/c hardware, software and control/ communication cable compatible VRF (DX type) AHU, IDU's system by Original equipment manufature (OEM). The unit operation on single phase AC supply 230V±10%, 50Hz by which following minimum operations/ facility can be done for min 30 units. 1) Operation display & history, ON/Off, Mode, Temp, Fans-peed, Fault /Error display/ record, Operation group/ individual etc complete as required. | item no.24 | 1 | No.
1.25 | Part (B) Low Side Works (Fitting items & accessories) | item no.25 | [52 empty] | 1.25 | Part (B) Low Side Works (Fitting items & accessories) | item no.25
1.26 | Refrigerant Piping | item no.26 | [52 empty] | 1.26 | Refrigerant Piping | item no.26
1.27 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of specified soft / hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/ with Class-O closed cell elastomeric Nitrile rubber tubular sleeves section specified thickness as given below for Suction and Liquid lines, all accessories with MS support complete as per specifications etc as required. | item no.27 | [52 empty] | 1.27 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of specified soft / hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/ with Class-O closed cell elastomeric Nitrile rubber tubular sleeves section specified thickness as given below for Suction and Liquid lines, all accessories with MS support complete as per specifications etc as required. | item no.27
1.28 | 6.4 mm dia (OD) tube thickness 0.8 mm with 13 mm thick insulation | item no.28 | 4 | Mtr | 220 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 880 | 880 | INR Eight Hundred & Eighty Only | 1.28 | 6.4 mm dia (OD) tube thickness 0.8 mm with 13 mm thick insulation | item no.28 | 4 | Mtr
1.29 | 9.5 mm dia (OD) tube thickness 0.8 mm with 13 mm thick insulation | item no.29 | 48 | Mtr | 320 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15360 | 15360 | INR Fifteen Thousand Three Hundred & Sixty Only | 1.29 | 9.5 mm dia (OD) tube thickness 0.8 mm with 13 mm thick insulation | item no.29 | 48 | Mtr
1.3 | 12.7 mm dia (OD) tube thickness 0.8 mm with 19 mm thick insulation | item no.30 | 12 | Mtr | 410 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4920 | 4920 | INR Four Thousand Nine Hundred & Twenty Only | 1.3 | 12.7 mm dia (OD) tube thickness 0.8 mm with 19 mm thick insulation | item no.30 | 12 | Mtr
1.31 | 15.86 mm dia(OD) tube thickness 1.2 mmwith 19 mm thick insulation | item no.31 | 38 | Mtr | 590 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 22420 | 22420 | INR Twenty Two Thousand Four Hundred & Twenty Only | 1.31 | 15.86 mm dia(OD) tube thickness 1.2 mmwith 19 mm thick insulation | item no.31 | 38 | Mtr
1.32 | 19.0 mm dia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.32 | 30 | Mtr | 640 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19200 | 19200 | INR Nineteen Thousand Two Hundred Only | 1.32 | 19.0 mm dia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.32 | 30 | Mtr
1.33 | 22.2 mm dia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.33 | 4 | Mtr | 750 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3000 | 3000 | INR Three Thousand Only | 1.33 | 22.2 mm dia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.33 | 4 | Mtr
1.34 | 25.4 mm dia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.34 | 15 | Mtr | 1150 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 17250 | 17250 | INR Seventeen Thousand Two Hundred & Fifty Only | 1.34 | 25.4 mm dia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.34 | 15 | Mtr
1.35 | 28.58 mmdia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.35 | 15 | Mtr | 1300 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19500 | 19500 | INR Nineteen Thousand Five Hundred Only | 1.35 | 28.58 mmdia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.35 | 15 | Mtr
1.36 | 31.08 mmdia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.36 | 4 | Mtr | 1450 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5800 | 5800 | INR Five Thousand Eight Hundred Only | 1.36 | 31.08 mmdia (OD) tube thickness 1.2 mm with 19 mm thick insulation | item no.36 | 4 | Mtr
1.37 | Top-up additional Refrigerant R-410a charging | item no.37 | [52 empty] | 1.37 | Top-up additional Refrigerant R-410a charging | item no.37
1.38 | Supply and charging/ refilling of additional R-410a (Du-pont/ approved make) Refrigerant Gas charging on VRF system complete as required. | item no.38 | 18 | Kg | 1000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 18000 | 18000 | INR Eighteen Thousand Only | 1.38 | Supply and charging/ refilling of additional R-410a (Du-pont/ approved make) Refrigerant Gas charging on VRF system complete as required. | item no.38 | 18 | Kg
1.39 | Power/Control and Communication cabling | item no.39 | [52 empty] | 1.39 | Power/Control and Communication cabling | item no.39
1.4 | Supply, laying, testing, and commissioning of following size (Shielded) PVC insulated Copper Communication cable in pvc conduit of following size on surface/recessed i/c clamping complete as required. | item no.40 | [52 empty] | 1.4 | Supply, laying, testing, and commissioning of following size (Shielded) PVC insulated Copper Communication cable in pvc conduit of following size on surface/recessed i/c clamping complete as required. | item no.40
1.41 | 2 core x 1.5 or 1.0 Sq mm, armoured/ Shielded copper cable | item no.41 | 210 | Mtr | 200 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 42000 | 42000 | INR Forty Two Thousand Only | 1.41 | 2 core x 1.5 or 1.0 Sq mm, armoured/ Shielded copper cable | item no.41 | 210 | Mtr
1.42 | Providing, laying, testing, and commissioning of following size FRLSH Un-armoured XLPE insulated Copper power/control cable in pvc hard/flexible conduit of following size on surface/recessed i/c Heavy duty copper lugs, Thimble , Glands termination, clamping/ties complete as required. | item no.42 | [52 empty] | 1.42 | Providing, laying, testing, and commissioning of following size FRLSH Un-armoured XLPE insulated Copper power/control cable in pvc hard/flexible conduit of following size on surface/recessed i/c Heavy duty copper lugs, Thimble , Glands termination, clamping/ties complete as required. | item no.42
1.43 | 3 Core x 1.5 Sq mm Unarmoured Copper Cable | item no.43 | 16 | Mtr | 180 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2880 | 2880 | INR Two Thousand Eight Hundred & Eighty Only | 1.43 | 3 Core x 1.5 Sq mm Unarmoured Copper Cable | item no.43 | 16 | Mtr
1.44 | 3 Core x 2.5 Sq mm Unarmoured Copper Cable | item no.44 | 16 | Mtr | 280 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4480 | 4480 | INR Four Thousand Four Hundred & Eighty Only | 1.44 | 3 Core x 2.5 Sq mm Unarmoured Copper Cable | item no.44 | 16 | Mtr
1.45 | 4 Core x 4.0 Sq mm Unarmoured Copper Cable | item no.45 | 12 | Mtr | 410 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4920 | 4920 | INR Four Thousand Nine Hundred & Twenty Only | 1.45 | 4 Core x 4.0 Sq mm Unarmoured Copper Cable | item no.45 | 12 | Mtr
1.46 | 4 Core x 16.0 Sq mm Unarmoured Copper Cable | item no.46 | 16 | Mtr | 720 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11520 | 11520 | INR Eleven Thousand Five Hundred & Twenty Only | 1.46 | 4 Core x 16.0 Sq mm Unarmoured Copper Cable | item no.46 | 16 | Mtr
1.47 | Condensate Drain uPVC Piping | item no.47 | [52 empty] | 1.47 | Condensate Drain uPVC Piping | item no.47
1.48 | Supply, installation, testing and commissioning of uPVC Pipe, complete with fittings, hanging supports, U trap arrangement, Clean Plug and accessories ect. complete as required. | item no.48 | [52 empty] | 1.48 | Supply, installation, testing and commissioning of uPVC Pipe, complete with fittings, hanging supports, U trap arrangement, Clean Plug and accessories ect. complete as required. | item no.48
1.49 | 32 mm dia (with 6 mm Nitrile insulation) | item no.49 | 40 | Mtr | 240 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9600 | 9600 | INR Nine Thousand Six Hundred Only | 1.49 | 32 mm dia (with 6 mm Nitrile insulation) | item no.49 | 40 | Mtr
1.5 | 40 mm dia (with 6 mm Nitrile insulation) | item no.50 | 40 | Mtr | 290 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11600 | 11600 | INR Eleven Thousand Six Hundred Only | 1.5 | 40 mm dia (with 6 mm Nitrile insulation) | item no.50 | 40 | Mtr
1.51 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/ round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | item no.51 | [52 empty] | 1.51 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/ round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | item no.51
1.52 | 24 Gauge | item no.52 | 90 | SqM | 928 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 83520 | 83520 | INR Eighty Three Thousand Five Hundred & Twenty Only | 1.52 | 24 Gauge | item no.52 | 90 | SqM
1.53 | 22 Gauge | item no.53 | 20 | SqM | 1078 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 21560 | 21560 | INR Twenty One Thousand Five Hundred & Sixty Only | 1.53 | 22 Gauge | item no.53 | 20 | SqM
1.54 | Supplying, fixing testing commissioning of Supply air Diffusers of powder coated aluminum with aluminum volume control dampers with anti smudge ring & removable core. | item no.54 | 5 | SqM | 10683 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 53415 | 53415 | INR Fifty Three Thousand Four Hundred & Fifteen Only | 1.54 | Supplying, fixing testing commissioning of Supply air Diffusers of powder coated aluminum with aluminum volume control dampers with anti smudge ring & removable core. | item no.54 | 5 | SqM
1.55 | Supplying, fixing testing commissioning of Return air Diffusers of powder coated aluminum without volume control dampers with anti smudge ring & removable core. | item no.55 | 7 | SqM | 7121 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 49847 | 49847 | INR Forty Nine Thousand Eight Hundred & Forty Seven Only | 1.55 | Supplying, fixing testing commissioning of Return air Diffusers of powder coated aluminum without volume control dampers with anti smudge ring & removable core. | item no.55 | 7 | SqM
1.56 | Supply & fixing of fire retardant double layer cloth canvass made (up to 300 mm vide) with heavy clothes and suitable frame with G.I washer, nuts & bolts in suitable size. i/c jointing both sides with suitable gaskets complete as reqd. | item no.56 | 4 | SqM | 3321 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 13284 | 13284 | INR Thirteen Thousand Two Hundred & Eighty Four Only | 1.56 | Supply & fixing of fire retardant double layer cloth canvass made (up to 300 mm vide) with heavy clothes and suitable frame with G.I washer, nuts & bolts in suitable size. i/c jointing both sides with suitable gaskets complete as reqd. | item no.56 | 4 | SqM
1.57 | Providing & fixing of thermal insulation without aluminium foil faced XLPE Class 'O' insulation sheet of following thickness on existing surface of pipe/duct with dentrite/adhesive etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminum tape complete as required. | item no.57 | [52 empty] | 1.57 | Providing & fixing of thermal insulation without aluminium foil faced XLPE Class 'O' insulation sheet of following thickness on existing surface of pipe/duct with dentrite/adhesive etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminum tape complete as required. | item no.57
1.58 | 19 mm | item no.58 | 100 | SqM | 534 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 53400 | 53400 | INR Fifty Three Thousand Four Hundred Only | 1.58 | 19 mm | item no.58 | 100 | SqM
1.59 | 13 mm | item no.59 | 10 | SqM | 305 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3050 | 3050 | INR Three Thousand &Fifty Only | 1.59 | 13 mm | item no.59 | 10 | SqM
1.6 | Providing & fixing of accoustic insulation with open cell nitrile rubber sheet (Accosound) supersilence of following thickness, on existing surface with adhesive i/c nut,bot washer as req on duct/Surface and accessories etc. complete as required. | item no.60 | [52 empty] | 1.6 | Providing & fixing of accoustic insulation with open cell nitrile rubber sheet (Accosound) supersilence of following thickness, on existing surface with adhesive i/c nut,bot washer as req on duct/Surface and accessories etc. complete as required. | item no.60
1.61 | 10 mm | item no.61 | 20 | SqM | 979 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19580 | 19580 | INR Nineteen Thousand Five Hundred & Eighty Only | 1.61 | 10 mm | item no.61 | 20 | SqM
1.62 | Providing & fixing of three phase DOL startar Suitable for following size motor, 415 Volts, with single phase preventer, wideband coil, ammeter, ON-OFF Push button etc. complete as required. | item no.62 | [52 empty] | 1.62 | Providing & fixing of three phase DOL startar Suitable for following size motor, 415 Volts, with single phase preventer, wideband coil, ammeter, ON-OFF Push button etc. complete as required. | item no.62
1.63 | Upto 5 H.P | item no.63 | 1 | No | 2783 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2783 | 2783 | INR Two Thousand Seven Hundred & Eighty Three Only | 1.63 | Upto 5 H.P | item no.63 | 1 | No
1.64 | Providing and fixing of Single Phase Plug top ISI Marked for AC (FCU) unit etc i/c dismantling old plug top if any complete as required. (Make:- Anchor or Equivalent) | item no.64 | [52 empty] | 1.64 | Providing and fixing of Single Phase Plug top ISI Marked for AC (FCU) unit etc i/c dismantling old plug top if any complete as required. (Make:- Anchor or Equivalent) | item no.64
1.65 | 3 pin- 6 Amp. | item no.65 | 5 | Nos | 136 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 680 | 680 | INR Six Hundred & Eighty Only | 1.65 | 3 pin- 6 Amp. | item no.65 | 5 | Nos
1.66 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthling as required. | item no.66 | 30 | Mtr | 62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1860 | 1860 | INR One Thousand Eight Hundred & Sixty Only | 1.66 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthling as required. | item no.66 | 30 | Mtr
1.67 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | item no.67 | 60 | Kg | 98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5880 | 5880 | INR Five Thousand Eight Hundred & Eighty Only | 1.67 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | item no.67 | 60 | Kg
1.68 | Supplying and Installing following size of perforated painted with powder coating M.S. cable trays with perforation not more then 17.5%, in convenient sections, joined with connectors, Suspended, from the ceiling with M.S.suspenders including bolts & nuts, painting suspenders ect. as required. | item no.68 | [52 empty] | 1.68 | Supplying and Installing following size of perforated painted with powder coating M.S. cable trays with perforation not more then 17.5%, in convenient sections, joined with connectors, Suspended, from the ceiling with M.S.suspenders including bolts & nuts, painting suspenders ect. as required. | item no.68
1.69 | 150 mm width X 50 mm depth X 1.6 mm thickness | item no.69 | 15 | Mtr | 604 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9060 | 9060 | INR Nine Thousand &Sixty Only | 1.69 | 150 mm width X 50 mm depth X 1.6 mm thickness | item no.69 | 15 | Mtr
1.7 | 300 mm width X 50 mm depth X 1.6 mm thickness | item no.70 | 15 | Mtr | 681 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10215 | 10215 | INR Ten Thousand Two Hundred & Fifteen Only | 1.7 | 300 mm width X 50 mm depth X 1.6 mm thickness | item no.70 | 15 | Mtr
1.71 | CMC of VRF System by OEM/Auth Vendor | item no.71 | [52 empty] | 1.71 | CMC of VRF System by OEM/Auth Vendor | item no.71
1.72 | Annual comprehensive maintenance contract of capacity as above annexure complete 38 hp VRF system by OEM/Auth Vendor which cover IDU,ODU, AHU, all spare parts, Compressor, PCB, Refrigerant, and consumables requirement software upgration, to run the VRF system of capacity 38 HP after expiring of 1 year (12 Months) defect liability period. | item no.72 | [52 empty] | 1.72 | Annual comprehensive maintenance contract of capacity as above annexure complete 38 hp VRF system by OEM/Auth Vendor which cover IDU,ODU, AHU, all spare parts, Compressor, PCB, Refrigerant, and consumables requirement software upgration, to run the VRF system of capacity 38 HP after expiring of 1 year (12 Months) defect liability period. | item no.72
1.73 | For 1st year (0-12 Months) | item no.73 | 4 | Qtr | 32000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 128000 | 128000 | INR One Lakh Twenty Eight Thousand Only | 1.73 | For 1st year (0-12 Months) | item no.73 | 4 | Qtr
Total in Figures | [51 empty] | 2475064 | #REF! | Twenty Four Lakh Seventy Five Thousand &Sixty Four Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Words |  | INR Zero Only
Note on K24: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K27: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K30: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K32: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K43: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K46: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K58: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.

## Macros
Please Enable Macros to View BoQ information