## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: Miscellaneous renovation works in various labs in academic area, IIT Kanpur (SH: Civil and Electrical)
NIT No: Composite/31/08/2023-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Component | [53 empty] | 1 | Component
1.01 | EARTH WORK | item no.1 | [52 empty] | 1.01 | EARTH WORK | item no.1 |  |  | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.02 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m : | item no.2 | [52 empty] | 1.02 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m : | item no.2
1.03 | All kinds of soil | item no.3 | [52 empty] | 1.03 | All kinds of soil | item no.3 |  |  | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | Pipes, cables etc, not exceeding 80 mm dia. | item no.4 | 27 | metre | 224.07 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6049.89 | 6049.89 | INR Six Thousand &Forty Nine and Paise Eighty Nine Only | 1.04 | Pipes, cables etc, not exceeding 80 mm dia. | item no.4 | 27 | metre
1.05 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. | item no.5 | [52 empty] | 1.05 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. | item no.5 |  |  | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | All kinds of soil. | item no.6 | 9.5 | cum | 251.51 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2389.35 | 2389.35 | INR Two Thousand Three Hundred & Eighty Nine and Paise Thirty Five Only | 1.06 | All kinds of soil. | item no.6 | 9.5 | cum
1.07 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | item no.7 | 7.15 | cum | 222.67 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1592.09 | 1592.09 | INR One Thousand Five Hundred & Ninety Two and Paise Nine Only | 1.07 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | item no.7 | 7.15 | cum
1.08 | Surface dressing of the ground including removing vegetation and in-equalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. | item no.8 | [52 empty] | 1.08 | Surface dressing of the ground including removing vegetation and in-equalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. | item no.8
1.09 | All kinds of soil | item no.9 | 48 | sqm | 24.68 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1184.64 | 1184.64 | INR One Thousand One Hundred & Eighty Four and Paise Sixty Four Only | 1.09 | All kinds of soil | item no.9 | 48 | sqm
1.1 | CEMENT CONCRETE (CAST IN SITU) | item no.10 | [52 empty] | 1.1 | CEMENT CONCRETE (CAST IN SITU) | item no.10 |  |  | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.11 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : | item no.11 | [52 empty] | 1.11 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : | item no.11
1.12 | 1:3:6 (1 Cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 40 mm nominal size derived from natural sources) | item no.12 | 1.25 | cum | 5848.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7310.66 | 7310.66 | INR Seven Thousand Three Hundred & Ten and Paise Sixty Six Only | 1.12 | 1:3:6 (1 Cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 40 mm nominal size derived from natural sources) | item no.12 | 1.25 | cum | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.13 | 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | item no.13 | 10.6 | cum | 5546.73 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 58795.34 | 58795.34 | INR Fifty Eight Thousand Seven Hundred & Ninety Five and Paise Thirty Four Only | 1.13 | 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | item no.13 | 10.6 | cum | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.14 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor etc., up to floor five level, excluding the cost of centering, shuttering and finishing: | item no.14 | [52 empty] | 1.14 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor etc., up to floor five level, excluding the cost of centering, shuttering and finishing: | item no.14
1.15 | 1:1½:3 (1 cement : 1½ coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | item no.15 | 0.2 | cum | 8587.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1717.45 | 1717.45 | INR One Thousand Seven Hundred & Seventeen and Paise Forty Five Only | 1.15 | 1:1½:3 (1 cement : 1½ coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | item no.15 | 0.2 | cum
1.16 | Providing and laying damp-proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 12.5mm nominal size derived from natural sources) | item no.16 | 3.08 | sqm | 325.16 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1001.49 | 1001.49 | INR One Thousand &One and Paise Forty Nine Only | 1.16 | Providing and laying damp-proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 12.5mm nominal size derived from natural sources) | item no.16 | 3.08 | sqm
1.17 | Providing & applying a coat of residual petroleum bitumen of grade of VG-10 of approved quality using 1.7kg per square metre on damp proof course after cleaning the surface with brushes and finally with apiece of cloth lightly soaked in kerosene oil. |  | 3.08 | sqm | 99.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 307.45 | 307.45 | INR Three Hundred & Seven and Paise Forty Five Only | 1.17 | Providing & applying a coat of residual petroleum bitumen of grade of VG-10 of approved quality using 1.7kg per square metre on damp proof course after cleaning the surface with brushes and finally with apiece of cloth lightly soaked in kerosene oil. |  | 3.08 | sqm
1.18 | Making plinth protection 50mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth. |  | 14.48 | sqm | 597.68 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8654.41 | 8654.41 | INR Eight Thousand Six Hundred & Fifty Four and Paise Forty One Only | 1.18 | Making plinth protection 50mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth. |  | 14.48 | sqm
1.19 | REINFORCED CEMENT CONCRETE | [53 empty] | 1.19 | REINFORCED CEMENT CONCRETE
1.2 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases above plinth level up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). |  | 4.56 | cum | 9398.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 42858.39 | 42858.39 | INR Forty Two Thousand Eight Hundred & Fifty Eight and Paise Thirty Nine Only | 1.2 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases above plinth level up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). |  | 4.56 | cum
1.21 | Centering and shuttering including strutting, propping etc. and removal of form for | [53 empty] | 1.21 | Centering and shuttering including strutting, propping etc. and removal of form for
1.22 | Shelves (Cast in situ) |  | 62.17 | sqm | 672.12 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 41785.7 | 41785.7 | INR Forty One Thousand Seven Hundred & Eighty Five and Paise Seventy Only | 1.22 | Shelves (Cast in situ) |  | 62.17 | sqm
1.23 | Lintels, beams, plinth beams, girders, bressumers and cantilevers |  | 5.75 | sqm | 533.41 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3067.11 | 3067.11 | INR Three Thousand &Sixty Seven and Paise Eleven Only | 1.23 | Lintels, beams, plinth beams, girders, bressumers and cantilevers |  | 5.75 | sqm
1.24 | Columns, Pillars, Piers, Abutments, Posts and Struts |  | 3.55 | sqm | 705.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2503.35 | 2503.35 | INR Two Thousand Five Hundred & Three and Paise Thirty Five Only | 1.24 | Columns, Pillars, Piers, Abutments, Posts and Struts |  | 3.55 | sqm
1.25 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. | [53 empty] | 1.25 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level.
1.26 | Thermo-Mechanically Treated bars of grade Fe-500D or more. |  | 536 | kg | 78.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 42134.96 | 42134.96 | INR Forty Two Thousand One Hundred & Thirty Four and Paise Ninety Six Only | 1.26 | Thermo-Mechanically Treated bars of grade Fe-500D or more. |  | 536 | kg
1.27 | MASONRY WORK | [53 empty] | 1.27 | MASONRY WORK
1.28 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level. | [53 empty] | 1.28 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.
1.29 | Cement mortar 1:4 (1 cement :4 coarse sand) |  | 86.53 | sqm | 892.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 77239.27 | 77239.27 | INR Seventy Seven Thousand Two Hundred & Thirty Nine and Paise Twenty Seven Only | 1.29 | Cement mortar 1:4 (1 cement :4 coarse sand) |  | 86.53 | sqm
1.3 | Brick work with common burnt clay selected F.P.S. (non modular) bricks of class designation 7.5 in exposed brick work including making horizontal and vertical grooves 10 mm wide 12 mm deep complete in cement mortar 1:6 (1 cement : 6 coarse sand) | [53 empty] | 1.3 | Brick work with common burnt clay selected F.P.S. (non modular) bricks of class designation 7.5 in exposed brick work including making horizontal and vertical grooves 10 mm wide 12 mm deep complete in cement mortar 1:6 (1 cement : 6 coarse sand)
1.31 | Above plinth level upto floor V level |  | 8.84 | cum | 7510.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 66394.59 | 66394.59 | INR Sixty Six Thousand Three Hundred & Ninety Four and Paise Fifty Nine Only | 1.31 | Above plinth level upto floor V level |  | 8.84 | cum
1.32 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: | [53 empty] | 1.32 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in:
1.33 | Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 3.3 | cum | 5838.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19265.43 | 19265.43 | INR Nineteen Thousand Two Hundred & Sixty Five and Paise Forty Three Only | 1.33 | Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 3.3 | cum
1.34 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : | [53 empty] | 1.34 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :
1.35 | Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 1 | cum | 7267.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7267.3 | 7267.3 | INR Seven Thousand Two Hundred & Sixty Seven and Paise Thirty Only | 1.35 | Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 1 | cum
1.36 | Brick edging 7cm wide 11.4 cm deep to plinth protection with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 including grouting with cement mortar 1:4 (1 cement : 4 fine sand). |  | 13.5 | metre | 48.93 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 660.56 | 660.56 | INR Six Hundred & Sixty and Paise Fifty Six Only | 1.36 | Brick edging 7cm wide 11.4 cm deep to plinth protection with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 including grouting with cement mortar 1:4 (1 cement : 4 fine sand). |  | 13.5 | metre
1.37 | CLADDING WORK | [53 empty] | 1.37 | CLADDING WORK
1.38 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. | [53 empty] | 1.38 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels.
1.39 | Granite stone slab colour black, Cherry/Ruby red | [53 empty] | 1.39 | Granite stone slab colour black, Cherry/Ruby red
1.4 | Area of slab over 0.50 sqm |  | 52.37 | sqm | 3880.18 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 203205.03 | 203205.03 | INR Two Lakh Three Thousand Two Hundred & Five and Paise Three Only | 1.4 | Area of slab over 0.50 sqm |  | 52.37 | sqm
1.41 | Extra for providing opening of required size & shape for wash basin/ kitchen sink in kitchen platform, vanity counter and similar location in marble/ Granite/ stone work, including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete. |  | 4 | each | 708.59 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2834.36 | 2834.36 | INR Two Thousand Eight Hundred & Thirty Four and Paise Thirty Six Only | 1.41 | Extra for providing opening of required size & shape for wash basin/ kitchen sink in kitchen platform, vanity counter and similar location in marble/ Granite/ stone work, including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete. |  | 4 | each
1.42 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. |  | 60.5 | sqm | 932.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 56412.62 | 56412.62 | INR Fifty Six Thousand Four Hundred & Twelve and Paise Sixty Two Only | 1.42 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. |  | 60.5 | sqm
1.43 | FLOORING | [53 empty] | 1.43 | FLOORING
1.44 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS: 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joints with white cement and matching pigments etc., complete. | [53 empty] | 1.44 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS: 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joints with white cement and matching pigments etc., complete.
1.45 | Size of Tile 600x600 mm |  | 51.88 | sqm | 1242.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 64441.7 | 64441.7 | INR Sixty Four Thousand Four Hundred & Forty One and Paise Seventy Only | 1.45 | Size of Tile 600x600 mm |  | 51.88 | sqm
1.46 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joint with white cement & matching pigments etc. complete. | [53 empty] | 1.46 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joint with white cement & matching pigments etc. complete.
1.47 | Size of Tile 600x600 mm |  | 1 | sqm | 1285.84 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1285.84 | 1285.84 | INR One Thousand Two Hundred & Eighty Five and Paise Eighty Four Only | 1.47 | Size of Tile 600x600 mm |  | 1 | sqm
1.48 | Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement, including cement slurry, but excluding the cost of nosing of steps etc. complete. | [53 empty] | 1.48 | Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement, including cement slurry, but excluding the cost of nosing of steps etc. complete.
1.49 | 40 mm thick with 20 mm nominal size stone aggregate |  | 21.2 | sqm | 477.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10130.63 | 10130.63 | INR Ten Thousand One Hundred & Thirty and Paise Sixty Three Only | 1.49 | 40 mm thick with 20 mm nominal size stone aggregate |  | 21.2 | sqm
1.5 | 62 mm thick cement concrete flooring with concrete hardener topping, under layer 50 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) and top layer 12mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate, 6mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacture’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc. complete. |  | 49 | sqm | 814.25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 39898.25 | 39898.25 | INR Thirty Nine Thousand Eight Hundred & Ninety Eight and Paise Twenty Five Only | 1.5 | 62 mm thick cement concrete flooring with concrete hardener topping, under layer 50 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) and top layer 12mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate, 6mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacture’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc. complete. |  | 49 | sqm
1.51 | Cement plaster skirting up to 30 cm height, with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement. | [53 empty] | 1.51 | Cement plaster skirting up to 30 cm height, with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement.
1.52 | 18 mm thick |  | 12 | sqm | 500.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6005.28 | 6005.28 | INR Six Thousand &Five and Paise Twenty Eight Only | 1.52 | 18 mm thick |  | 12 | sqm
1.53 | Cement concrete pavement with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), including finishing complete. |  | 1.08 | cum | 6978.21 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7536.47 | 7536.47 | INR Seven Thousand Five Hundred & Thirty Six and Paise Forty Seven Only | 1.53 | Cement concrete pavement with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), including finishing complete. |  | 1.08 | cum
1.54 | Providing and fixing glass strips in joints of terrazo/ cement concrete floors. | [53 empty] | 1.54 | Providing and fixing glass strips in joints of terrazo/ cement concrete floors.
1.55 | 40 mm wide and 4 mm thick |  | 124 | metre | 69.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8644.04 | 8644.04 | INR Eight Thousand Six Hundred & Forty Four and Paise Four Only | 1.55 | 40 mm wide and 4 mm thick |  | 124 | metre
1.56 | WOOD AND P. V. C. WORK | [53 empty] | 1.56 | WOOD AND P. V. C. WORK
1.57 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters: | [53 empty] | 1.57 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters:
1.58 | 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws |  | 10.92 | sqm | 1767.43 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19300.34 | 19300.34 | INR Nineteen Thousand Three Hundred and Paise Thirty Four Only | 1.58 | 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws |  | 10.92 | sqm
1.59 | Extra for cutting rebate in flush door shutters (Total area of the shutter to be measured). |  | 3.15 | sqm | 82.11 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 258.65 | 258.65 | INR Two Hundred & Fifty Eight and Paise Sixty Five Only | 1.59 | Extra for cutting rebate in flush door shutters (Total area of the shutter to be measured). |  | 3.15 | sqm
1.6 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. | [53 empty] | 1.6 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete.
1.61 | Fixed to steel windows by welding |  | 230 | kg | 158.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 36501 | 36501 | INR Thirty Six Thousand Five Hundred & One Only | 1.61 | Fixed to steel windows by welding |  | 230 | kg
1.62 | Providing and fixing ISI marked oxidised M.S. sliding door bolts with nuts and screws etc. complete : | [53 empty] | 1.62 | Providing and fixing ISI marked oxidised M.S. sliding door bolts with nuts and screws etc. complete :
1.63 | 300x16 mm |  | 1 | each | 158.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 158.31 | 158.31 | INR One Hundred & Fifty Eight and Paise Thirty One Only | 1.63 | 300x16 mm |  | 1 | each
1.64 | Providing and fixing ISI marked oxidised M.S. handles conforming to IS:4992 with necessary screws etc. complete : | [53 empty] | 1.64 | Providing and fixing ISI marked oxidised M.S. handles conforming to IS:4992 with necessary screws etc. complete :
1.65 | 125 mm |  | 2 | each | 30.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 61.72 | 61.72 | INR Sixty One and Paise Seventy Two Only | 1.65 | 125 mm |  | 2 | each
1.66 | 100 mm |  | 14 | each | 24.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 346.78 | 346.78 | INR Three Hundred & Forty Six and Paise Seventy Eight Only | 1.66 | 100 mm |  | 14 | each
1.67 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. complete. | [53 empty] | 1.67 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. complete.
1.68 | 250 mm weighing not less than 150 grams |  | 10 | each | 45.51 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 455.1 | 455.1 | INR Four Hundred & Fifty Five and Paise Ten Only | 1.68 | 250 mm weighing not less than 150 grams |  | 10 | each
1.69 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm), with necessary accessories and screws etc. complete. |  | 5 | each | 899.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4496.5 | 4496.5 | INR Four Thousand Four Hundred & Ninety Six and Paise Fifty Only | 1.69 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm), with necessary accessories and screws etc. complete. |  | 5 | each
1.7 | Providing and fixing aluminium sliding door bolts, ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete : | [53 empty] | 1.7 | Providing and fixing aluminium sliding door bolts, ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete :
1.71 | 250x16 mm |  | 2 | each | 205.96 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 411.92 | 411.92 | INR Four Hundred & Eleven and Paise Ninety Two Only | 1.71 | 250x16 mm |  | 2 | each
1.72 | 300x16 mm |  | 2 | each | 228.23 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 456.46 | 456.46 | INR Four Hundred & Fifty Six and Paise Forty Six Only | 1.72 | 300x16 mm |  | 2 | each
1.73 | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete : | [53 empty] | 1.73 | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete :
1.74 | 250x10 mm |  | 8 | each | 91.54 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 732.32 | 732.32 | INR Seven Hundred & Thirty Two and Paise Thirty Two Only | 1.74 | 250x10 mm |  | 8 | each
1.75 | 150x10 mm |  | 32 | each | 66.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2119.68 | 2119.68 | INR Two Thousand One Hundred & Nineteen and Paise Sixty Eight Only | 1.75 | 150x10 mm |  | 32 | each
1.76 | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete : | [53 empty] | 1.76 | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete :
1.77 | 125 mm |  | 14 | each | 52.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 737.1 | 737.1 | INR Seven Hundred & Thirty Seven and Paise Ten Only | 1.77 | 125 mm |  | 14 | each
1.78 | 100 mm |  | 16 | each | 46.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 747.04 | 747.04 | INR Seven Hundred & Forty Seven and Paise Four Only | 1.78 | 100 mm |  | 16 | each
1.79 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete. | [53 empty] | 1.79 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete.
1.8 | Twin rubber stopper |  | 6 | each | 54.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 327.48 | 327.48 | INR Three Hundred & Twenty Seven and Paise Forty Eight Only | 1.8 | Twin rubber stopper |  | 6 | each
1.81 | Extra for providing lipping with 2nd class teak wood battens 25 mm minimum depth on all edges of flush door shutters (over all area of door shutter to be measured). |  | 5.67 | sqm | 351.95 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1995.56 | 1995.56 | INR One Thousand Nine Hundred & Ninety Five and Paise Fifty Six Only | 1.81 | Extra for providing lipping with 2nd class teak wood battens 25 mm minimum depth on all edges of flush door shutters (over all area of door shutter to be measured). |  | 5.67 | sqm
1.82 | Extra for providing vision panel not exceeding 0.1 sqm in all type of flush doors (cost of glass excluded) (overall area of door shutter to be measured): | [53 empty] | 1.82 | Extra for providing vision panel not exceeding 0.1 sqm in all type of flush doors (cost of glass excluded) (overall area of door shutter to be measured):
1.83 | Rectangular or square |  | 3.78 | sqm | 152.52 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 576.53 | 576.53 | INR Five Hundred & Seventy Six and Paise Fifty Three Only | 1.83 | Rectangular or square |  | 3.78 | sqm
1.84 | Providing and fixing bright finished brass 100 mm mortice latch and lock with 6 levers and a pair of lever handles of approved quality with necessary screws etc. complete. |  | 2 | each | 634.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1269.26 | 1269.26 | INR One Thousand Two Hundred & Sixty Nine and Paise Twenty Six Only | 1.84 | Providing and fixing bright finished brass 100 mm mortice latch and lock with 6 levers and a pair of lever handles of approved quality with necessary screws etc. complete. |  | 2 | each
1.85 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm(both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete. | [53 empty] | 1.85 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm(both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete.
1.86 | 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) plaster board conforming to IS: 2095: part 3 (Board with BIS certification marks) |  | 79 | sqm | 1576.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 124519.01 | 124519.01 | INR One Lakh Twenty Four Thousand Five Hundred & Nineteen and Paise One Only | 1.86 | 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) plaster board conforming to IS: 2095: part 3 (Board with BIS certification marks) |  | 79 | sqm
1.87 | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt/ suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S, including cost of adhesive of approved quality. | [53 empty] | 1.87 | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt/ suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S, including cost of adhesive of approved quality.
1.88 | 1.0 mm thick |  | 11.34 | sqm | 669.88 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7596.44 | 7596.44 | INR Seven Thousand Five Hundred & Ninety Six and Paise Forty Four Only | 1.88 | 1.0 mm thick |  | 11.34 | sqm
1.89 | Providing and fixing frame work for partitions/ wall lining etc. made of 50x50x1.6 mm hollow MS tube, placed along the walls, ceiling and floor in a grid pattern with spacing @ 60 cm centre to centre both ways (vertically & horizontally) or at required spacing near opening, with necessary welding at junctions and fixing the frame to wall/ ceiling/ floors with steel dash fasteners of 8 mm dia, 75 mm long bolt, including making provision for opening for doors, windows, electrical conduits, switch boards etc., including providing with two coats of approved steel primer etc. complete, all as per direction of Engineer-in-charge. |  | 205 | kg | 116.92 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 23968.6 | 23968.6 | INR Twenty Three Thousand Nine Hundred & Sixty Eight and Paise Sixty Only | 1.89 | Providing and fixing frame work for partitions/ wall lining etc. made of 50x50x1.6 mm hollow MS tube, placed along the walls, ceiling and floor in a grid pattern with spacing @ 60 cm centre to centre both ways (vertically & horizontally) or at required spacing near opening, with necessary welding at junctions and fixing the frame to wall/ ceiling/ floors with steel dash fasteners of 8 mm dia, 75 mm long bolt, including making provision for opening for doors, windows, electrical conduits, switch boards etc., including providing with two coats of approved steel primer etc. complete, all as per direction of Engineer-in-charge. |  | 205 | kg
1.9 | Providing and fixing bright finished brass 100 mm mortice latch and lock, ISI marked, with six levers and a pair of anodised (anodic coating not less than grade AC 10 as per IS : 1868) aluminium lever handles of approved quality with necessary screws etc. complete. |  | 1 | each | 648.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 648.66 | 648.66 | INR Six Hundred & Forty Eight and Paise Sixty Six Only | 1.9 | Providing and fixing bright finished brass 100 mm mortice latch and lock, ISI marked, with six levers and a pair of anodised (anodic coating not less than grade AC 10 as per IS : 1868) aluminium lever handles of approved quality with necessary screws etc. complete. |  | 1 | each
1.91 | Providing and fixing sliding arrangement in racks/ cupboards/cabinets shutter by with stainless steel rollers to run inside C or E aluminium channel section (The payment of C or E channel shall be made separately) |  | 2 | each | 15.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 30.96 | 30.96 | INR Thirty and Paise Ninety Six Only | 1.91 | Providing and fixing sliding arrangement in racks/ cupboards/cabinets shutter by with stainless steel rollers to run inside C or E aluminium channel section (The payment of C or E channel shall be made separately) |  | 2 | each
1.92 | Providing and fixing plain lining with necessary screws/nuts & bolts/ nails, including a coat of approved primer on one face, and fixed on wooden /steel frame work, complete as per direction of Engineer-in- charge (Frame work shall be paid for separately). | [53 empty] | 1.92 | Providing and fixing plain lining with necessary screws/nuts & bolts/ nails, including a coat of approved primer on one face, and fixed on wooden /steel frame work, complete as per direction of Engineer-in- charge (Frame work shall be paid for separately).
1.93 | 12mm thick commercial ply conforming to IS : 1328 BWR type |  | 0.5 | sqm | 950.99 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 475.5 | 475.5 | INR Four Hundred & Seventy Five and Paise Fifty Only | 1.93 | 12mm thick commercial ply conforming to IS : 1328 BWR type |  | 0.5 | sqm
1.94 | STEEL WORK | [53 empty] | 1.94 | STEEL WORK
1.95 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6 mm angle iron and 3 mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer. | [53 empty] | 1.95 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6 mm angle iron and 3 mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer.
1.96 | Using M.S. angels 40x40x6 mm for diagonal braces |  | 2.56 | sqm | 4192.15 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10731.9 | 10731.9 | INR Ten Thousand Seven Hundred & Thirty One and Paise Ninety Only | 1.96 | Using M.S. angels 40x40x6 mm for diagonal braces |  | 2.56 | sqm
1.97 | Providing and fixing T-iron frames for doors, windows and ventilators of mild steel Tee-sections, joints mitred and welded, including fixing of necessary butt hinges and screws and applying a priming coat of approved steel primer. | [53 empty] | 1.97 | Providing and fixing T-iron frames for doors, windows and ventilators of mild steel Tee-sections, joints mitred and welded, including fixing of necessary butt hinges and screws and applying a priming coat of approved steel primer.
1.98 | Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). |  | 93 | kg | 100.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9349.29 | 9349.29 | INR Nine Thousand Three Hundred & Forty Nine and Paise Twenty Nine Only | 1.98 | Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). |  | 93 | kg
1.99 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required. | [53 empty] | 1.99 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required.
2 | In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works |  | 180.25 | kg | 124.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 22489.79 | 22489.79 | INR Twenty Two Thousand Four Hundred & Eighty Nine and Paise Seventy Nine Only | 2 | In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works |  | 180.25 | kg
2.01 | Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 mm dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge. | [53 empty] | 2.01 | Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 mm dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge.
2.02 | 10 x 80 mm |  | 56 | each | 102.85 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5759.6 | 5759.6 | INR Five Thousand Seven Hundred & Fifty Nine and Paise Sixty Only | 2.02 | 10 x 80 mm |  | 56 | each
2.03 | Providing and fixing factory made ISI marked steel glazed doors, windows and ventilators, side /top /centre hung, with beading and all members such as F7D,F4B, K11 B and K12 B etc. complete of standard rolled steel sections, joints mitred and flash butt welded and sash bars tenoned and riveted, including providing and fixing of hinges, pivots, including priming coat of approved steel primer, but excluding the cost of other fittings, complete all as per approved design, (sectional weight of only steel members shall be measured for payment). | [53 empty] | 2.03 | Providing and fixing factory made ISI marked steel glazed doors, windows and ventilators, side /top /centre hung, with beading and all members such as F7D,F4B, K11 B and K12 B etc. complete of standard rolled steel sections, joints mitred and flash butt welded and sash bars tenoned and riveted, including providing and fixing of hinges, pivots, including priming coat of approved steel primer, but excluding the cost of other fittings, complete all as per approved design, (sectional weight of only steel members shall be measured for payment).
2.04 | Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) |  | 20 | kg | 154.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3080.2 | 3080.2 | INR Three Thousand &Eighty and Paise Twenty Only | 2.04 | Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) |  | 20 | kg
2.05 | Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 mm dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge. | [53 empty] | 2.05 | Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 mm dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge.
2.06 | 10 x 60 mm |  | 44 | each | 97.94 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4309.36 | 4309.36 | INR Four Thousand Three Hundred & Nine and Paise Thirty Six Only | 2.06 | 10 x 60 mm |  | 44 | each
2.07 | Providing & fixing glass panes with putty and glazing clips in steel doors, windows, clerestory windows, all complete with : | [53 empty] | 2.07 | Providing & fixing glass panes with putty and glazing clips in steel doors, windows, clerestory windows, all complete with :
2.08 | 5.5 mm thick glass panes |  | 0.5 | sqm | 1090.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 545.16 | 545.16 | INR Five Hundred & Forty Five and Paise Sixteen Only | 2.08 | 5.5 mm thick glass panes |  | 0.5 | sqm
2.09 | ROOFING | [53 empty] | 2.09 | ROOFING
2.1 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. | [53 empty] | 2.1 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes.
2.11 | 110 mm diameter |  | 51.4 | metre | 280.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14410.5 | 14410.5 | INR Fourteen Thousand Four Hundred & Ten and Paise Fifty Only | 2.11 | 110 mm diameter |  | 51.4 | metre
2.12 | Providing & fixing UV stabilised fiberglass reinforced plastic sheet roofing up to any pitch, including fixing with polymer coated 'J' or 'L' hooks, bolts & nuts 8mm dia. G.I plain/bitumen washers complete but excluding the cost of purlins, rafters, trusses etc. The sheets shall be manufactured out of 2400 TEX panel rovigs incorporating minimum 0.3% ultra-violet stabiliser in resin system under approximately 2400 psi and hot cured. They shall be of uniform pigmentation and thickness without air pockets and shall conform to IS 10192 and IS 12866.The sheets shall be opaque or translucent, clear or pigmented, textured or smooth as specified. | [53 empty] | 2.12 | Providing & fixing UV stabilised fiberglass reinforced plastic sheet roofing up to any pitch, including fixing with polymer coated 'J' or 'L' hooks, bolts & nuts 8mm dia. G.I plain/bitumen washers complete but excluding the cost of purlins, rafters, trusses etc. The sheets shall be manufactured out of 2400 TEX panel rovigs incorporating minimum 0.3% ultra-violet stabiliser in resin system under approximately 2400 psi and hot cured. They shall be of uniform pigmentation and thickness without air pockets and shall conform to IS 10192 and IS 12866.The sheets shall be opaque or translucent, clear or pigmented, textured or smooth as specified.
2.13 | 2 mm thick corrugated (2.5" or 4.2" or 6") or step-down (2" or 3" or 6" ) as specified |  | 20 | sqm | 1033.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 20679.6 | 20679.6 | INR Twenty Thousand Six Hundred & Seventy Nine and Paise Sixty Only | 2.13 | 2 mm thick corrugated (2.5" or 4.2" or 6") or step-down (2" or 3" or 6" ) as specified |  | 20 | sqm
2.14 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-charge) 0.50 mm (+ 0.05 %) total coated thickness with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer- in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. |  | 1.9 | sqm | 588.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1118.76 | 1118.76 | INR One Thousand One Hundred & Eighteen and Paise Seventy Six Only | 2.14 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-charge) 0.50 mm (+ 0.05 %) total coated thickness with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer- in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. |  | 1.9 | sqm
2.15 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge. | [53 empty] | 2.15 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge.
2.16 | 12.5 mm thick square edge PVC Laminated Gypsum Tile of size 595x595 mm, made of Gypsum plasterboard, manufactured from natural gypsum as per IS 2095 part I and laminated with white 0.16mm thick fire retardant PVC film on the face side and 12micron metalized polyester on the back side with all edges sealed with the face side PVC film which goes around and wraps the edges and is bonded to the edges and the back side metalized polyester film so as to make the tile a completely sealed unit. |  | 120 | sqm | 1708.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 205063.2 | 205063.2 | INR Two Lakh Five Thousand &Sixty Three and Paise Twenty Only | 2.16 | 12.5 mm thick square edge PVC Laminated Gypsum Tile of size 595x595 mm, made of Gypsum plasterboard, manufactured from natural gypsum as per IS 2095 part I and laminated with white 0.16mm thick fire retardant PVC film on the face side and 12micron metalized polyester on the back side with all edges sealed with the face side PVC film which goes around and wraps the edges and is bonded to the edges and the back side metalized polyester film so as to make the tile a completely sealed unit. |  | 120 | sqm
2.17 | Providing and fixing thermal insulation with Resin Bonded Fibre glass wool conforming to IS: 8183 having density 24 kg/m3, 50 mm thick, wrapped in 200G Virgin Polythene Bags fixed to wall with screw, rawel plug & washers and held in position by criss crossing GI wire etc. complete as per directions of Engineer-in-Charge. |  | 79 | sqm | 269.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 21289.71 | 21289.71 | INR Twenty One Thousand Two Hundred & Eighty Nine and Paise Seventy One Only | 2.17 | Providing and fixing thermal insulation with Resin Bonded Fibre glass wool conforming to IS: 8183 having density 24 kg/m3, 50 mm thick, wrapped in 200G Virgin Polythene Bags fixed to wall with screw, rawel plug & washers and held in position by criss crossing GI wire etc. complete as per directions of Engineer-in-Charge. |  | 79 | sqm
2.18 | FINISHING | [53 empty] | 2.18 | FINISHING
2.19 | 12 mm cement plaster of mix : | [53 empty] | 2.19 | 12 mm cement plaster of mix :
2.2 | 1:6 (1 cement: 6 coarse sand) |  | 88.2 | sqm | 258.09 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 22763.54 | 22763.54 | INR Twenty Two Thousand Seven Hundred & Sixty Three and Paise Fifty Four Only | 2.2 | 1:6 (1 cement: 6 coarse sand) |  | 88.2 | sqm
2.21 | 6 mm cement plaster of mix : | [53 empty] | 2.21 | 6 mm cement plaster of mix :
2.22 | 1:3 (1 cement : 3 fine sand) |  | 51.06 | sqm | 221.88 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11329.19 | 11329.19 | INR Eleven Thousand Three Hundred & Twenty Nine and Paise Nineteen Only | 2.22 | 1:3 (1 cement : 3 fine sand) |  | 51.06 | sqm
2.23 | 15 mm cement plaster on rough side of single or half brick wall of mix: | [53 empty] | 2.23 | 15 mm cement plaster on rough side of single or half brick wall of mix:
2.24 | 1:6 (1 cement: 6 coarse sand) |  | 110 | sqm | 297.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 32706.3 | 32706.3 | INR Thirty Two Thousand Seven Hundred & Six and Paise Thirty Only | 2.24 | 1:6 (1 cement: 6 coarse sand) |  | 110 | sqm
2.25 | Pointing on brick work or brick flooring with cement mortar 1:3 (1 cement : 3 fine sand): | [53 empty] | 2.25 | Pointing on brick work or brick flooring with cement mortar 1:3 (1 cement : 3 fine sand):
2.26 | Flush / Ruled/ Struck or weathered pointing |  | 39 | sqm | 187.99 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7331.61 | 7331.61 | INR Seven Thousand Three Hundred & Thirty One and Paise Sixty One Only | 2.26 | Flush / Ruled/ Struck or weathered pointing |  | 39 | sqm
2.27 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gms/litre, of approved manufacturer, of required shade and colour complete, as per manufacturer's specification. | [53 empty] | 2.27 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gms/litre, of approved manufacturer, of required shade and colour complete, as per manufacturer's specification.
2.28 | Two or more coats on new work |  | 877.2 | sqm | 81.32 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 71333.9 | 71333.9 | INR Seventy One Thousand Three Hundred & Thirty Three and Paise Ninety Only | 2.28 | Two or more coats on new work |  | 877.2 | sqm
2.29 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : | [53 empty] | 2.29 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :
2.3 | Two or more coats on new work |  | 32 | sqm | 115.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3688.32 | 3688.32 | INR Three Thousand Six Hundred & Eighty Eight and Paise Thirty Two Only | 2.3 | Two or more coats on new work |  | 32 | sqm
2.31 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. |  | 877.2 | sqm | 108.59 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 95255.15 | 95255.15 | INR Ninety Five Thousand Two Hundred & Fifty Five and Paise Fifteen Only | 2.31 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. |  | 877.2 | sqm
2.32 | Distempering with 1st quality acrylic distember (Ready mix) having VOC content less than 50 grams/ litre of approved brand and manufacture to give an even shade : | [53 empty] | 2.32 | Distempering with 1st quality acrylic distember (Ready mix) having VOC content less than 50 grams/ litre of approved brand and manufacture to give an even shade :
2.33 | Old work (one or more coats) |  | 320 | sqm | 49.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15936 | 15936 | INR Fifteen Thousand Nine Hundred & Thirty Six Only | 2.33 | Old work (one or more coats) |  | 320 | sqm
2.34 | Finishing walls with Acrylic Smooth exterior paint of required shade : | [53 empty] | 2.34 | Finishing walls with Acrylic Smooth exterior paint of required shade :
2.35 | New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) |  | 85 | sqm | 146.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 12435.5 | 12435.5 | INR Twelve Thousand Four Hundred & Thirty Five and Paise Fifty Only | 2.35 | New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) |  | 85 | sqm
2.36 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : | [53 empty] | 2.36 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade :
2.37 | One or more coats on old work |  | 33.15 | sqm | 75.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2515.75 | 2515.75 | INR Two Thousand Five Hundred & Fifteen and Paise Seventy Five Only | 2.37 | One or more coats on old work |  | 33.15 | sqm
2.38 | Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture |  | 13 | sqm | 167.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2181.66 | 2181.66 | INR Two Thousand One Hundred & Eighty One and Paise Sixty Six Only | 2.38 | Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture |  | 13 | sqm
2.39 | Removing dry or oil bound distemper, water proofing cement paint and the like by scrapping, sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete. |  | 538 | sqm | 18.28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9834.64 | 9834.64 | INR Nine Thousand Eight Hundred & Thirty Four and Paise Sixty Four Only | 2.39 | Removing dry or oil bound distemper, water proofing cement paint and the like by scrapping, sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete. |  | 538 | sqm
2.4 | REPAIRS TO BUILDING | [53 empty] | 2.4 | REPAIRS TO BUILDING
2.41 | Hacking of CC flooring including cleaning for surface etc. complete as per direction of the Engineer-in-Charge. |  | 45.43 | sqm | 2.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 113.58 | 113.58 | INR One Hundred & Thirteen and Paise Fifty Eight Only | 2.41 | Hacking of CC flooring including cleaning for surface etc. complete as per direction of the Engineer-in-Charge. |  | 45.43 | sqm
2.42 | Repairs to plaster of thickness 12 mm to 20 mm in patches of area 2.5 sq.meters and under, including cutting the patch in proper shape, raking out joints and preparing and plastering the surface of the walls complete, including disposal of rubbish to the dumping ground, all complete as per direction of Engineer-in-Charge. | [53 empty] | 2.42 | Repairs to plaster of thickness 12 mm to 20 mm in patches of area 2.5 sq.meters and under, including cutting the patch in proper shape, raking out joints and preparing and plastering the surface of the walls complete, including disposal of rubbish to the dumping ground, all complete as per direction of Engineer-in-Charge.
2.43 | With cement mortar 1:4 (1cement: 4 coarse sand) |  | 13 | sqm | 419.11 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5448.43 | 5448.43 | INR Five Thousand Four Hundred & Forty Eight and Paise Forty Three Only | 2.43 | With cement mortar 1:4 (1cement: 4 coarse sand) |  | 13 | sqm
2.44 | Making the opening in brick masonry including dismantling in floor or walls by cutting masonry and making good the damages to walls, flooring and jambs complete, to match existing surface i/c disposal of mulba/ rubbish to the nearest municipal dumping ground, all complete as per direction of Engineer-in-Charge. | [53 empty] | 2.44 | Making the opening in brick masonry including dismantling in floor or walls by cutting masonry and making good the damages to walls, flooring and jambs complete, to match existing surface i/c disposal of mulba/ rubbish to the nearest municipal dumping ground, all complete as per direction of Engineer-in-Charge.
2.45 | For door/ window/ clerestory window |  | 3.15 | sqm | 917.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2891.61 | 2891.61 | INR Two Thousand Eight Hundred & Ninety One and Paise Sixty One Only | 2.45 | For door/ window/ clerestory window |  | 3.15 | sqm
2.46 | Cutting holes of required size in brick masonry wall for fixing of exhaust fan including providing and fixing 300 mm dia PVC pipe conforming BIS-12818 and making good the same etc. complete as per direction of Engineer-in-charge. |  | 1 | each | 213.15 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 213.15 | 213.15 | INR Two Hundred & Thirteen and Paise Fifteen Only | 2.46 | Cutting holes of required size in brick masonry wall for fixing of exhaust fan including providing and fixing 300 mm dia PVC pipe conforming BIS-12818 and making good the same etc. complete as per direction of Engineer-in-charge. |  | 1 | each
2.47 | Renewing glass panes, with putty and nails wherever necessary including racking out the old putty: | [53 empty] | 2.47 | Renewing glass panes, with putty and nails wherever necessary including racking out the old putty:
2.48 | Float glass panes of nominal thickness 4 mm (weight not less than 10kg/sqm) |  | 18 | sqm | 825.91 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14866.38 | 14866.38 | INR Fourteen Thousand Eight Hundred & Sixty Six and Paise Thirty Eight Only | 2.48 | Float glass panes of nominal thickness 4 mm (weight not less than 10kg/sqm) |  | 18 | sqm
2.49 | Dismantling and Demolishing | [53 empty] | 2.49 | Dismantling and Demolishing
2.5 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead. |  | 44 | sqm | 39.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1738 | 1738 | INR One Thousand Seven Hundred & Thirty Eight Only | 2.5 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead. |  | 44 | sqm
2.51 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | [53 empty] | 2.51 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.
2.52 | Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) |  | 2.5 | cum | 1759.84 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4399.6 | 4399.6 | INR Four Thousand Three Hundred & Ninety Nine and Paise Sixty Only | 2.52 | Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) |  | 2.5 | cum
2.53 | Nominal concrete 1:4:8 or leaner mix (i/c equivalent design mix) |  | 5.83 | cum | 1086.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6336.57 | 6336.57 | INR Six Thousand Three Hundred & Thirty Six and Paise Fifty Seven Only | 2.53 | Nominal concrete 1:4:8 or leaner mix (i/c equivalent design mix) |  | 5.83 | cum
2.54 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. |  | 1.35 | cum | 2567.38 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3465.96 | 3465.96 | INR Three Thousand Four Hundred & Sixty Five and Paise Ninety Six Only | 2.54 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. |  | 1.35 | cum
2.55 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. | [53 empty] | 2.55 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.
2.56 | In cement mortar |  | 10.04 | cum | 1489.22 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14951.77 | 14951.77 | INR Fourteen Thousand Nine Hundred & Fifty One and Paise Seventy Seven Only | 2.56 | In cement mortar |  | 10.04 | cum
2.57 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead : | [53 empty] | 2.57 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :
2.58 | Of area 3 sq. metres and below |  | 7 | each | 265.41 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1857.87 | 1857.87 | INR One Thousand Eight Hundred & Fifty Seven and Paise Eighty Seven Only | 2.58 | Of area 3 sq. metres and below |  | 7 | each
2.59 | Of area beyond 3 sq. metres |  | 4 | each | 363.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1453.92 | 1453.92 | INR One Thousand Four Hundred & Fifty Three and Paise Ninety Two Only | 2.59 | Of area beyond 3 sq. metres |  | 4 | each
2.6 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead. | [53 empty] | 2.6 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.
2.61 | For thickness of tiles 10 mm to 25 mm |  | 3.43 | sqm | 53.05 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 181.96 | 181.96 | INR One Hundred & Eighty One and Paise Ninety Six Only | 2.61 | For thickness of tiles 10 mm to 25 mm |  | 3.43 | sqm
2.62 | Taking out doors, windows and clerestory window shutters (steel or wood) including stacking within 50 metres lead : | [53 empty] | 2.62 | Taking out doors, windows and clerestory window shutters (steel or wood) including stacking within 50 metres lead :
2.63 | Of area 3 sq. metres and below |  | 1 | each | 103.73 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 103.73 | 103.73 | INR One Hundred & Three and Paise Seventy Three Only | 2.63 | Of area 3 sq. metres and below |  | 1 | each
2.64 | Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge. |  | 6 | sqm | 40.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 244.62 | 244.62 | INR Two Hundred & Forty Four and Paise Sixty Two Only | 2.64 | Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge. |  | 6 | sqm
2.65 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all leads including all lifts involved. |  | 5 | cum | 192.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 961.65 | 961.65 | INR Nine Hundred & Sixty One and Paise Sixty Five Only | 2.65 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all leads including all lifts involved. |  | 5 | cum
2.66 | SANITARY INSTALLATIONS | [53 empty] | 2.66 | SANITARY INSTALLATIONS
2.67 | Providing and fixing white vitreous china laboratory sink including making all connections excluding cost of fittings : | [53 empty] | 2.67 | Providing and fixing white vitreous china laboratory sink including making all connections excluding cost of fittings :
2.68 | Size 600x450x200 mm |  | 5 | each | 3060.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15300.95 | 15300.95 | INR Fifteen Thousand Three Hundred and Paise Ninety Five Only | 2.68 | Size 600x450x200 mm |  | 5 | each
2.69 | Providing and fixing P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete. | [53 empty] | 2.69 | Providing and fixing P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete.
2.7 | Flexible pipe | [53 empty] | 2.7 | Flexible pipe
2.71 | 32 mm dia |  | 5 | each | 91.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 457.45 | 457.45 | INR Four Hundred & Fifty Seven and Paise Forty Five Only | 2.71 | 32 mm dia |  | 5 | each
2.72 | WATER SUPPLY | [53 empty] | 2.72 | WATER SUPPLY
2.73 | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc. Internal work - Exposed on wall | [53 empty] | 2.73 | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc. Internal work - Exposed on wall
2.74 | 15 mm dia nominal bore |  | 7.5 | metre | 266.68 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2000.1 | 2000.1 | INR Two Thousand and Paise Ten Only | 2.74 | 15 mm dia nominal bore |  | 7.5 | metre
2.75 | 20 mm dia nominal bore |  | 48 | metre | 327.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15713.28 | 15713.28 | INR Fifteen Thousand Seven Hundred & Thirteen and Paise Twenty Eight Only | 2.75 | 20 mm dia nominal bore |  | 48 | metre
2.76 | 25 mm dia nominal bore |  | 20 | metre | 430.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8613.8 | 8613.8 | INR Eight Thousand Six Hundred & Thirteen and Paise Eighty Only | 2.76 | 25 mm dia nominal bore |  | 20 | metre
2.77 | 40 mm dia nominal bore |  | 13 | metre | 635.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8265.66 | 8265.66 | INR Eight Thousand Two Hundred & Sixty Five and Paise Sixty Six Only | 2.77 | 40 mm dia nominal bore |  | 13 | metre
2.78 | Making connection of G.I. distribution branch with G.I. main of following sizes by providing and fixing tee, including cutting and threading the pipe etc. complete : | [53 empty] | 2.78 | Making connection of G.I. distribution branch with G.I. main of following sizes by providing and fixing tee, including cutting and threading the pipe etc. complete :
2.79 | 25 to 40 mm nominal bore |  | 7 | each | 663.83 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4646.81 | 4646.81 | INR Four Thousand Six Hundred & Forty Six and Paise Eighty One Only | 2.79 | 25 to 40 mm nominal bore |  | 7 | each
2.8 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : | [53 empty] | 2.8 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :
2.81 | 20 mm nominal bore |  | 6 | each | 404.87 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2429.22 | 2429.22 | INR Two Thousand Four Hundred & Twenty Nine and Paise Twenty Two Only | 2.81 | 20 mm nominal bore |  | 6 | each
2.82 | 25 mm nominal bore |  | 1 | each | 466.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 466.77 | 466.77 | INR Four Hundred & Sixty Six and Paise Seventy Seven Only | 2.82 | 25 mm nominal bore |  | 1 | each
2.83 | Constructing masonry Chamber 30x30x50 cm inside, in brick work in cement mortar 1:4 (1 cement :4 coarse sand) for stop cock, with C. I. surface box 100x100 x75 mm (inside) with hinged cover fixed in cement concrete slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), i/c necessary excavation, foundation concrete 1:5:10 ( 1 cement : 5 fine sand : 10 graded stone aggregate 40mm nominal size ) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12mm thick, finished with a floating coat of neat cement complete as per standard design : | [53 empty] | 2.83 | Constructing masonry Chamber 30x30x50 cm inside, in brick work in cement mortar 1:4 (1 cement :4 coarse sand) for stop cock, with C. I. surface box 100x100 x75 mm (inside) with hinged cover fixed in cement concrete slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), i/c necessary excavation, foundation concrete 1:5:10 ( 1 cement : 5 fine sand : 10 graded stone aggregate 40mm nominal size ) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12mm thick, finished with a floating coat of neat cement complete as per standard design :
2.84 | With common burnt clay F.P.S.(non modular) bricks of class designation 7.5 |  | 2 | each | 1501.23 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3002.46 | 3002.46 | INR Three Thousand &Two and Paise Forty Six Only | 2.84 | With common burnt clay F.P.S.(non modular) bricks of class designation 7.5 |  | 2 | each
2.85 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. | [53 empty] | 2.85 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.
2.86 | 15 mm nominal bore |  | 6 | each | 621.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3726.78 | 3726.78 | INR Three Thousand Seven Hundred & Twenty Six and Paise Seventy Eight Only | 2.86 | 15 mm nominal bore |  | 6 | each
2.87 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 | [53 empty] | 2.87 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931
2.88 | 15mm nominal bore |  | 13 | each | 438.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5703.23 | 5703.23 | INR Five Thousand Seven Hundred & Three and Paise Twenty Three Only | 2.88 | 15mm nominal bore |  | 13 | each
2.89 | Providing and fixing G.I. Union in existing G.I. pipe line, cutting and threading the pipe and making long screws, including excavation, refilling the earth or cutting of wall and making good the same complete wherever required : | [53 empty] | 2.89 | Providing and fixing G.I. Union in existing G.I. pipe line, cutting and threading the pipe and making long screws, including excavation, refilling the earth or cutting of wall and making good the same complete wherever required :
2.9 | 20 mm nominal bore |  | 2 | each | 622.27 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1244.54 | 1244.54 | INR One Thousand Two Hundred & Forty Four and Paise Fifty Four Only | 2.9 | 20 mm nominal bore |  | 2 | each
2.91 | 25 mm nominal bore |  | 2 | each | 692.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1385.26 | 1385.26 | INR One Thousand Three Hundred & Eighty Five and Paise Twenty Six Only | 2.91 | 25 mm nominal bore |  | 2 | each
2.92 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. | [53 empty] | 2.92 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931.
2.93 | 15 mm nominal bore |  | 1 | each | 521.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 521.48 | 521.48 | INR Five Hundred & Twenty One and Paise Forty Eight Only | 2.93 | 15 mm nominal bore |  | 1 | each
2.94 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall | [53 empty] | 2.94 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall
2.95 | 15 mm nominal dia Pipes |  | 10 | metre | 224.38 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2243.8 | 2243.8 | INR Two Thousand Two Hundred & Forty Three and Paise Eighty Only | 2.95 | 15 mm nominal dia Pipes |  | 10 | metre
2.96 | 20 mm nominal dia Pipes |  | 13 | metre | 285.05 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3705.65 | 3705.65 | INR Three Thousand Seven Hundred & Five and Paise Sixty Five Only | 2.96 | 20 mm nominal dia Pipes |  | 13 | metre
2.97 | 40 mm nominal dia Pipes |  | 12.5 | metre | 591.28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7391 | 7391 | INR Seven Thousand Three Hundred & Ninety One Only | 2.97 | 40 mm nominal dia Pipes |  | 12.5 | metre
2.98 | Cutting holes up to 30x30 cm in walls including making good the same: | [53 empty] | 2.98 | Cutting holes up to 30x30 cm in walls including making good the same:
2.99 | With common burnt clay F.P.S. (non modular) bricks |  | 4 | each | 317.76 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1271.04 | 1271.04 | INR One Thousand Two Hundred & Seventy One and Paise Four Only | 2.99 | With common burnt clay F.P.S. (non modular) bricks |  | 4 | each
3 | ALUMINIUM WORK | [53 empty] | 3 | ALUMINIUM WORK
3.01 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : | [53 empty] | 3.01 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) :
3.02 | For fixed portion | [53 empty] | 3.02 | For fixed portion
3.03 | Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) |  | 155.6 | kg | 380.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 59204.24 | 59204.24 | INR Fifty Nine Thousand Two Hundred & Four and Paise Twenty Four Only | 3.03 | Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) |  | 155.6 | kg
3.04 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately) | [53 empty] | 3.04 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately)
3.05 | Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) |  | 91.8 | kg | 466.29 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 42805.42 | 42805.42 | INR Forty Two Thousand Eight Hundred & Five and Paise Forty Two Only | 3.05 | Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) |  | 91.8 | kg
3.06 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): | [53 empty] | 3.06 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item):
3.07 | With float glass panes of 5 mm thickness (weight not less than 12.50 kg/sqm) |  | 19.63 | sqm | 1162.25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 22814.97 | 22814.97 | INR Twenty Two Thousand Eight Hundred & Fourteen and Paise Ninety Seven Only | 3.07 | With float glass panes of 5 mm thickness (weight not less than 12.50 kg/sqm) |  | 19.63 | sqm
3.08 | Providing and fixing stainless steel (SS 304 grade) adjustable friction windows stays of approved quality with necessary stainless steel screws etc. to the side hung windows as per direction of Engineer- in-charge complete. | [53 empty] | 3.08 | Providing and fixing stainless steel (SS 304 grade) adjustable friction windows stays of approved quality with necessary stainless steel screws etc. to the side hung windows as per direction of Engineer- in-charge complete.
3.09 | 255 X 19 mm |  | 16 | each | 288.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4618.4 | 4618.4 | INR Four Thousand Six Hundred & Eighteen and Paise Forty Only | 3.09 | 255 X 19 mm |  | 16 | each
3.1 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer- in-charge. | [53 empty] | 3.1 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer- in-charge.
3.11 | Pre-laminated particle board with decorative lamination on both sides |  | 1 | sqm | 833.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 833.89 | 833.89 | INR Eight Hundred & Thirty Three and Paise Eighty Nine Only | 3.11 | Pre-laminated particle board with decorative lamination on both sides |  | 1 | sqm
3.12 | Providing and fixing Brass 100mm mortice latch and lock with 6 levers without pair of handles (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. |  | 1 | each | 394.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 394.17 | 394.17 | INR Three Hundred & Ninety Four and Paise Seventeen Only | 3.12 | Providing and fixing Brass 100mm mortice latch and lock with 6 levers without pair of handles (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. |  | 1 | each
3.13 | NEW TECHNOLOGIES AND MATERIALS | [53 empty] | 3.13 | NEW TECHNOLOGIES AND MATERIALS
3.14 | Chipping of unsound/weak concrete material from slabs, beams, columns etc. with manual Chisel and/ or by standard power driven percussion type or of approved make including tapering of all edges, making square shoulders of cavities including cleaning the exposed concrete surface and reinforcement with wire brushes etc. and disposal of debris for all lead and lifts all complete as per direction of Engineer-In-Charge | [53 empty] | 3.14 | Chipping of unsound/weak concrete material from slabs, beams, columns etc. with manual Chisel and/ or by standard power driven percussion type or of approved make including tapering of all edges, making square shoulders of cavities including cleaning the exposed concrete surface and reinforcement with wire brushes etc. and disposal of debris for all lead and lifts all complete as per direction of Engineer-In-Charge
3.15 | 50mm average thickness |  | 4 | sqm | 185.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 741.96 | 741.96 | INR Seven Hundred & Forty One and Paise Ninety Six Only | 3.15 | 50mm average thickness |  | 4 | sqm
3.16 | Providing, mixing and applying bonding coat of approved adhesive on chipped portion of RCC as per specifications and direction of Engineer-In-charge complete in all respect. | [53 empty] | 3.16 | Providing, mixing and applying bonding coat of approved adhesive on chipped portion of RCC as per specifications and direction of Engineer-In-charge complete in all respect.
3.17 | SBR Polymer (@10% of cement weight) modified cementitious bond coat @ 2.2 kg cement per sqm of surface area mixed with specified proportion of approved polymer |  | 4 | sqm | 103.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 412.96 | 412.96 | INR Four Hundred & Twelve and Paise Ninety Six Only | 3.17 | SBR Polymer (@10% of cement weight) modified cementitious bond coat @ 2.2 kg cement per sqm of surface area mixed with specified proportion of approved polymer |  | 4 | sqm
3.18 | Providing, mixing and applying SBR polymer (of approved make) modified Cement mortar in proportion of 1:4 (1 cement: 4 graded coarse sand with polymer minimum 2% by wt. of cement used) as per specifications and directions of Engineer-in-charge. | [53 empty] | 3.18 | Providing, mixing and applying SBR polymer (of approved make) modified Cement mortar in proportion of 1:4 (1 cement: 4 graded coarse sand with polymer minimum 2% by wt. of cement used) as per specifications and directions of Engineer-in-charge.
3.19 | 50 mm average thickness in 3 layers. |  | 4 | sqm | 895.18 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3580.72 | 3580.72 | INR Three Thousand Five Hundred & Eighty and Paise Seventy Two Only | 3.19 | 50 mm average thickness in 3 layers. |  | 4 | sqm
3.2 | DRAINAGE | [53 empty] | 3.2 | DRAINAGE
3.21 | Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement and making necessary channels for the drain etc. complete : | [53 empty] | 3.21 | Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement and making necessary channels for the drain etc. complete :
3.22 | For pipes 100 to 250 mm diameter |  | 2 | each | 599.47 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1198.94 | 1198.94 | INR One Thousand One Hundred & Ninety Eight and Paise Ninety Four Only | 3.22 | For pipes 100 to 250 mm diameter |  | 2 | each
3.23 | MINOR CIVIL MAINTENANCE WORK: | [53 empty] | 3.23 | MINOR CIVIL MAINTENANCE WORK:
3.24 | Removal of old PVC floor and proper scrapping, cleaning etc to prepare surface for reflooring as per direction incharge. |  | 103 | Sqm | 42.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4352.78 | 4352.78 | INR Four Thousand Three Hundred & Fifty Two and Paise Seventy Eight Only | 3.24 | Removal of old PVC floor and proper scrapping, cleaning etc to prepare surface for reflooring as per direction incharge. |  | 103 | Sqm
3.25 | P/F homogeneous polyvinyl chloride sheet 2.00 mm thick in flooring and skirting in approved pattern on a smooth and damp proof base using rubber base adhesive of approved quality and manufacturer like Dunlop S-758 , Fevicol SR 998 or equivalent including rolling with light wooden roller weight about 5 kg. All complete as directed by Engineer -in -charge in approved color & shade. |  | 52 | Sqm | 632.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 32891.56 | 32891.56 | INR Thirty Two Thousand Eight Hundred & Ninety One and Paise Fifty Six Only | 3.25 | P/F homogeneous polyvinyl chloride sheet 2.00 mm thick in flooring and skirting in approved pattern on a smooth and damp proof base using rubber base adhesive of approved quality and manufacturer like Dunlop S-758 , Fevicol SR 998 or equivalent including rolling with light wooden roller weight about 5 kg. All complete as directed by Engineer -in -charge in approved color & shade. |  | 52 | Sqm
3.26 | "P/F 1.50mm thick homogeneous polyvinyl chloride sheet/tile in flooring and skirting in approved pattern on a smooth and damp proof base using rubber base adhesive of approved quality and manufacturer like Dualpo S-758 , Fevicol SR 998 or equivalent including rolling with light wooden roller weight about 5 kg. All complete as directed by Engineer -in -charge in approved colour and shade. |  | 127 | Sqm | 542.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 68927.98 | 68927.98 | INR Sixty Eight Thousand Nine Hundred & Twenty Seven and Paise Ninety Eight Only | 3.26 | "P/F 1.50mm thick homogeneous polyvinyl chloride sheet/tile in flooring and skirting in approved pattern on a smooth and damp proof base using rubber base adhesive of approved quality and manufacturer like Dualpo S-758 , Fevicol SR 998 or equivalent including rolling with light wooden roller weight about 5 kg. All complete as directed by Engineer -in -charge in approved colour and shade. |  | 127 | Sqm
3.27 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated, copper conductor, single core cable in surface/ recessed steel conduit as reqired. | [53 empty] | 3.27 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated, copper conductor, single core cable in surface/ recessed steel conduit as reqired.
3.28 | 4 x 6 Sqmm. + 2 x 06 sqmm earth wire |  | 15 | Mtr. | 661.11 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9916.65 | 9916.65 | INR Nine Thousand Nine Hundred & Sixteen and Paise Sixty Five Only | 3.28 | 4 x 6 Sqmm. + 2 x 06 sqmm earth wire |  | 15 | Mtr.
3.29 | 4 x 10 Sqmm. + 2 x 06 sqmm earth wire |  | 90 | Mtr. | 1022.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 92012.4 | 92012.4 | INR Ninety Two Thousand &Twelve and Paise Forty Only | 3.29 | 4 x 10 Sqmm. + 2 x 06 sqmm earth wire |  | 90 | Mtr.
3.3 | Supplying & drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel / PVC conduit as reqd. | [53 empty] | 3.3 | Supplying & drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel / PVC conduit as reqd.
3.31 | 1 x 1.5 Sq.mm.. |  | 80 | Mtr. | 39.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3156.8 | 3156.8 | INR Three Thousand One Hundred & Fifty Six and Paise Eighty Only | 3.31 | 1 x 1.5 Sq.mm.. |  | 80 | Mtr.
3.32 | 3 x 1.5 Sq.mm.. |  | 650 | Mtr. | 83.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 54145 | 54145 | INR Fifty Four Thousand One Hundred & Forty Five Only | 3.32 | 3 x 1.5 Sq.mm.. |  | 650 | Mtr.
3.33 | 3 x 2.5 sq. mm |  | 135 | Mtr. | 120.12 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 16216.2 | 16216.2 | INR Sixteen Thousand Two Hundred & Sixteen and Paise Twenty Only | 3.33 | 3 x 2.5 sq. mm |  | 135 | Mtr.
3.34 | 3 x 4 Sq.mm.. |  | 880 | Mtr. | 180.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 158963.2 | 158963.2 | INR One Lakh Fifty Eight Thousand Nine Hundred & Sixty Three and Paise Twenty Only | 3.34 | 3 x 4 Sq.mm.. |  | 880 | Mtr.
3.35 | 4 x 16 Sq.mm.. |  | 5 | Mtr. | 1039.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5199.45 | 5199.45 | INR Five Thousand One Hundred & Ninety Nine and Paise Forty Five Only | 3.35 | 4 x 16 Sq.mm.. |  | 5 | Mtr.
3.36 | 3 x 35 Sq.mm.. |  | 5 | Mtr. | 1669.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8347.2 | 8347.2 | INR Eight Thousand Three Hundred & Forty Seven and Paise Twenty Only | 3.36 | 3 x 35 Sq.mm.. |  | 5 | Mtr.
3.37 | 4 x 35 Sq.mm.. |  | 25 | Mtr. | 2214.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 55370.5 | 55370.5 | INR Fifty Five Thousand Three Hundred & Seventy and Paise Fifty Only | 3.37 | 4 x 35 Sq.mm.. |  | 25 | Mtr.
3.38 | 6 x 6 sq. mm |  | 80 | Metre | 524.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 41946.4 | 41946.4 | INR Forty One Thousand Nine Hundred & Forty Six and Paise Forty Only | 3.38 | 6 x 6 sq. mm |  | 80 | Metre
3.39 | 3 x 16 sq.mm. |  | 35 | Meter | 780.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 27312.6 | 27312.6 | INR Twenty Seven Thousand Three Hundred & Twelve and Paise Sixty Only | 3.39 | 3 x 16 sq.mm. |  | 35 | Meter
3.4 | 2 x 16 sq.mm. |  | 25 | Meter | 533.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 13327.5 | 13327.5 | INR Thirteen Thousand Three Hundred & Twenty Seven and Paise Fifty Only | 3.4 | 2 x 16 sq.mm. |  | 25 | Meter
3.41 | 6 x 16 sq.mm. |  | 55 | Meter | 1523.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 83813.95 | 83813.95 | INR Eighty Three Thousand Eight Hundred & Thirteen and Paise Ninety Five Only | 3.41 | 6 x 16 sq.mm. |  | 55 | Meter
3.42 | S & F metal box of following sizes ( nominal size ) on surface or in recess with suitable size of phenolic laminated sheet cover in the front I/c painting etc as reqd. | [53 empty] | 3.42 | S & F metal box of following sizes ( nominal size ) on surface or in recess with suitable size of phenolic laminated sheet cover in the front I/c painting etc as reqd.
3.43 | 250 mm x 300 mm x 100 mm deep |  | 1 | Nos. | 572.56 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 572.56 | 572.56 | INR Five Hundred & Seventy Two and Paise Fifty Six Only | 3.43 | 250 mm x 300 mm x 100 mm deep |  | 1 | Nos.
3.44 | 200 mm X 300 mm X 100 mm deep |  | 3 | No. | 491.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1475.67 | 1475.67 | INR One Thousand Four Hundred & Seventy Five and Paise Sixty Seven Only | 3.44 | 200 mm X 300 mm X 100 mm deep |  | 3 | No.
3.45 | Supply, fixing, following modular type switch / socket on existing modular plate & switch box including connectins but excluding modular plate etc. as reqd. | [53 empty] | 3.45 | Supply, fixing, following modular type switch / socket on existing modular plate & switch box including connectins but excluding modular plate etc. as reqd.
3.46 | 5/6 Amp switch |  | 37 | Nos. | 90.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3341.47 | 3341.47 | INR Three Thousand Three Hundred & Forty One and Paise Forty Seven Only | 3.46 | 5/6 Amp switch |  | 37 | Nos.
3.47 | 15/16 Amp. switch |  | 1 | Nos. | 136.78 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 136.78 | 136.78 | INR One Hundred & Thirty Six and Paise Seventy Eight Only | 3.47 | 15/16 Amp. switch |  | 1 | Nos.
3.48 | 3 Pin 5/6 Amp. socket outlet |  | 1 | Nos. | 106.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 106.97 | 106.97 | INR One Hundred & Six and Paise Ninety Seven Only | 3.48 | 3 Pin 5/6 Amp. socket outlet |  | 1 | Nos.
3.49 | 6 Pin 15/16 Amp. socket outlet. |  | 1 | Nos. | 172.73 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 172.73 | 172.73 | INR One Hundred & Seventy Two and Paise Seventy Three Only | 3.49 | 6 Pin 15/16 Amp. socket outlet. |  | 1 | Nos.
3.5 | Blanking plate |  | 10 | Nos. | 35.07 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 350.7 | 350.7 | INR Three Hundred & Fifty and Paise Seventy Only | 3.5 | Blanking plate |  | 10 | Nos.
3.51 | S/F following modular base & cover plate on existing modular metal boxes etc. as reqd. | [53 empty] | 3.51 | S/F following modular base & cover plate on existing modular metal boxes etc. as reqd.
3.52 | 1 or 2 module |  | 1 | Nos. | 116.62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 116.62 | 116.62 | INR One Hundred & Sixteen and Paise Sixty Two Only | 3.52 | 1 or 2 module |  | 1 | Nos.
3.53 | 3 module |  | 1 | Nos. | 132.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 132.4 | 132.4 | INR One Hundred & Thirty Two and Paise Forty Only | 3.53 | 3 module |  | 1 | Nos.
3.54 | 4 module |  | 1 | Nos. | 138.54 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 138.54 | 138.54 | INR One Hundred & Thirty Eight and Paise Fifty Four Only | 3.54 | 4 module |  | 1 | Nos.
3.55 | 6 module |  | 1 | Nos. | 159.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 159.58 | 159.58 | INR One Hundred & Fifty Nine and Paise Fifty Eight Only | 3.55 | 6 module |  | 1 | Nos.
3.56 | 8 module |  | 1 | Nos. | 185.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 185.01 | 185.01 | INR One Hundred & Eighty Five and Paise One Only | 3.56 | 8 module |  | 1 | Nos.
3.57 | 12 module |  | 3 | Nos. | 238.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 715.47 | 715.47 | INR Seven Hundred & Fifteen and Paise Forty Seven Only | 3.57 | 12 module |  | 3 | Nos.
3.58 | Supplying and fixing following size/ surface mounting plastic box as required.make havells OR equivalent approved make. | [53 empty] | 3.58 | Supplying and fixing following size/ surface mounting plastic box as required.make havells OR equivalent approved make.
3.59 | 1/2 module |  | 1 | Nos. | 272.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 272.69 | 272.69 | INR Two Hundred & Seventy Two and Paise Sixty Nine Only | 3.59 | 1/2 module |  | 1 | Nos.
3.6 | 3 module |  | 1 | Nos. | 284.96 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 284.96 | 284.96 | INR Two Hundred & Eighty Four and Paise Ninety Six Only | 3.6 | 3 module |  | 1 | Nos.
3.61 | 4 module |  | 1 | Nos. | 297.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 297.24 | 297.24 | INR Two Hundred & Ninety Seven and Paise Twenty Four Only | 3.61 | 4 module |  | 1 | Nos.
3.62 | 6 module |  | 1 | Nos. | 331.43 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 331.43 | 331.43 | INR Three Hundred & Thirty One and Paise Forty Three Only | 3.62 | 6 module |  | 1 | Nos.
3.63 | Supplying and fixing of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mmx50mmetc as required to complete of approved make ( Arteor model of Legrand or equivalent). | [53 empty] | 3.63 | Supplying and fixing of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mmx50mmetc as required to complete of approved make ( Arteor model of Legrand or equivalent).
3.64 | 1 or 2 module |  | 5 | Nos. | 225.34 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1126.7 | 1126.7 | INR One Thousand One Hundred & Twenty Six and Paise Seventy Only | 3.64 | 1 or 2 module |  | 5 | Nos.
3.65 | 3 module |  | 50 | Nos. | 300.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15037.5 | 15037.5 | INR Fifteen Thousand &Thirty Seven and Paise Fifty Only | 3.65 | 3 module |  | 50 | Nos.
3.66 | 6 module |  | 55 | Nos. | 403.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 22183.15 | 22183.15 | INR Twenty Two Thousand One Hundred & Eighty Three and Paise Fifteen Only | 3.66 | 6 module |  | 55 | Nos.
3.67 | Supplying and fixing of following ways surface/ recess mounting, of Virtical three phase distribution board with provision for 4 ploe MCCB upto 160A as incommer , of sheet steel, dust protected, duly powder painted, inclusive of 200 A, tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCCBs ( up to with 160A MCCBs as incomer) complete as required and instructed by Engineer in charge. | [53 empty] | 3.67 | Supplying and fixing of following ways surface/ recess mounting, of Virtical three phase distribution board with provision for 4 ploe MCCB upto 160A as incommer , of sheet steel, dust protected, duly powder painted, inclusive of 200 A, tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCCBs ( up to with 160A MCCBs as incomer) complete as required and instructed by Engineer in charge.
3.68 | 8-way(TmaxXT1+24) double door |  | 1 | Nos. | 15384.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15384.48 | 15384.48 | INR Fifteen Thousand Three Hundred & Eighty Four and Paise Forty Eight Only | 3.68 | 8-way(TmaxXT1+24) double door |  | 1 | Nos.
3.69 | Supplying and fixing 5 amps to 32 amps rating, 240 volts, 'C' series, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as reqd. | [53 empty] | 3.69 | Supplying and fixing 5 amps to 32 amps rating, 240 volts, 'C' series, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as reqd.
3.7 | Single Pole |  | 69 | Nos. | 224.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15487.74 | 15487.74 | INR Fifteen Thousand Four Hundred & Eighty Seven and Paise Seventy Four Only | 3.7 | Single Pole |  | 69 | Nos.
3.71 | Single Pole & Neutral |  | 1 | Nos. | 525.21 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 525.21 | 525.21 | INR Five Hundred & Twenty Five and Paise Twenty One Only | 3.71 | Single Pole & Neutral |  | 1 | Nos.
3.72 | Triple Pole |  | 16 | Nos. | 882.95 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14127.2 | 14127.2 | INR Fourteen Thousand One Hundred & Twenty Seven and Paise Twenty Only | 3.72 | Triple Pole |  | 16 | Nos.
3.73 | Triple pole & Neutral |  | 12 | Nos. | 1076.72 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 12920.64 | 12920.64 | INR Twelve Thousand Nine Hundred & Twenty and Paise Sixty Four Only | 3.73 | Triple pole & Neutral |  | 12 | Nos.
3.74 | S & F 40 amp to 63 amp rating 240 volts 'C' curve 10 kA MCB of following pole in the existing MCB DB complete with connection, testing & commissioning etc as reqd. | [53 empty] | 3.74 | S & F 40 amp to 63 amp rating 240 volts 'C' curve 10 kA MCB of following pole in the existing MCB DB complete with connection, testing & commissioning etc as reqd.
3.75 | Single Pole |  | 11 | Nos. | 719.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7918.46 | 7918.46 | INR Seven Thousand Nine Hundred & Eighteen and Paise Forty Six Only | 3.75 | Single Pole |  | 11 | Nos.
3.76 | Double pole |  | 2 | Nos. | 1341.52 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2683.04 | 2683.04 | INR Two Thousand Six Hundred & Eighty Three and Paise Four Only | 3.76 | Double pole |  | 2 | Nos.
3.77 | Triple Pole |  | 7 | Nos. | 2427.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 16989.07 | 16989.07 | INR Sixteen Thousand Nine Hundred & Eighty Nine and Paise Seven Only | 3.77 | Triple Pole |  | 7 | Nos.
3.78 | Four Pole |  | 4 | Nos. | 3037.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 12149.04 | 12149.04 | INR Twelve Thousand One Hundred & Forty Nine and Paise Four Only | 3.78 | Four Pole |  | 4 | Nos.
3.79 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32 A 240 V "C" curve DP MCB complete with connections, testing and commissioning etc. as required. |  | 1 | Nos. | 1024.99 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1024.99 | 1024.99 | INR One Thousand &Twenty Four and Paise Ninety Nine Only | 3.79 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32 A 240 V "C" curve DP MCB complete with connections, testing and commissioning etc. as required. |  | 1 | Nos.
3.8 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32 A 415 V "C" curve TP MCB complete with connections, testing and commissioning etc. as required. |  | 1 | Nos. | 1395.88 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1395.88 | 1395.88 | INR One Thousand Three Hundred & Ninety Five and Paise Eighty Eight Only | 3.8 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32 A 415 V "C" curve TP MCB complete with connections, testing and commissioning etc. as required. |  | 1 | Nos.
3.81 | P & F 6 SWG dia GI wire on surface or in recess for loop earthing as reqd. |  | 45 | Mtr. | 61.38 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2762.1 | 2762.1 | INR Two Thousand Seven Hundred & Sixty Two and Paise Ten Only | 3.81 | P & F 6 SWG dia GI wire on surface or in recess for loop earthing as reqd. |  | 45 | Mtr.
3.82 | Supplying and making indoor end termination with brass compression gland, aluminum lugs for following size of PVC insulated & PVC sheathed/XLPE aluminum cable of 1.1kV grade as reqd. | [53 empty] | 3.82 | Supplying and making indoor end termination with brass compression gland, aluminum lugs for following size of PVC insulated & PVC sheathed/XLPE aluminum cable of 1.1kV grade as reqd.
3.83 | 3 X 150 sq. mm (50mm) |  | 2 | Nos. | 371.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 743.54 | 743.54 | INR Seven Hundred & Forty Three and Paise Fifty Four Only | 3.83 | 3 X 150 sq. mm (50mm) |  | 2 | Nos.
3.84 | Providing and fixing DLP plastic trunking of size 105 mm x 50 mm without cover on surface as reqd. |  | 275 | Mtr. | 976.76 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 268609 | 268609 | INR Two Lakh Sixty Eight Thousand Six Hundred & Nine Only | 3.84 | Providing and fixing DLP plastic trunking of size 105 mm x 50 mm without cover on surface as reqd. |  | 275 | Mtr.
3.85 | Providing and fixing 85 mm width flexible cover of DLP plastic trunking. (size 105 mm x 50 mm.) |  | 265 | Mtr. | 432.27 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 114551.55 | 114551.55 | INR One Lakh Fourteen Thousand Five Hundred & Fifty One and Paise Fifty Five Only | 3.85 | Providing and fixing 85 mm width flexible cover of DLP plastic trunking. (size 105 mm x 50 mm.) |  | 265 | Mtr.
3.86 | Supply and fixing of following items for plastic trunking accessories suitable for size 105 mm x 50 mm. | [53 empty] | 3.86 | Supply and fixing of following items for plastic trunking accessories suitable for size 105 mm x 50 mm.
3.87 | End cap |  | 25 | Nos. | 194.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4866.25 | 4866.25 | INR Four Thousand Eight Hundred & Sixty Six and Paise Twenty Five Only | 3.87 | End cap |  | 25 | Nos.
3.88 | Internal angle. |  | 26 | Nos. | 539.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14020.24 | 14020.24 | INR Fourteen Thousand &Twenty and Paise Twenty Four Only | 3.88 | Internal angle. |  | 26 | Nos.
3.89 | Flat Junction |  | 28 | Nos. | 938.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 26269.32 | 26269.32 | INR Twenty Six Thousand Two Hundred & Sixty Nine and Paise Thirty Two Only | 3.89 | Flat Junction |  | 28 | Nos.
3.9 | Base joint |  | 65 | Nos. | 224.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14589.9 | 14589.9 | INR Fourteen Thousand Five Hundred & Eighty Nine and Paise Ninety Only | 3.9 | Base joint |  | 65 | Nos.
3.91 | external angles- adjustable from 60°-120° |  | 11 | Nos. | 550.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6057.04 | 6057.04 | INR Six Thousand &Fifty Seven and Paise Four Only | 3.91 | external angles- adjustable from 60°-120° |  | 11 | Nos.
3.92 | flat angles |  | 5 | Nos. | 762.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3814.1 | 3814.1 | INR Three Thousand Eight Hundred & Fourteen and Paise Ten Only | 3.92 | flat angles |  | 5 | Nos.
3.93 | separation partitions |  | 70 | Meter | 260.41 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 18228.7 | 18228.7 | INR Eighteen Thousand Two Hundred & Twenty Eight and Paise Seventy Only | 3.93 | separation partitions |  | 70 | Meter
3.94 | base joints |  | 102 | Nos. | 90.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9211.62 | 9211.62 | INR Nine Thousand Two Hundred & Eleven and Paise Sixty Two Only | 3.94 | base joints |  | 102 | Nos.
3.95 | Supplying, installation DLP mini- trunking 32mm x 20mm and accessories white-system with independent cover- without central partion etc. as reqd. | [53 empty] | 3.95 | Supplying, installation DLP mini- trunking 32mm x 20mm and accessories white-system with independent cover- without central partion etc. as reqd.
3.96 | Mini- trunking |  | 75 | Mtr. | 227.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 17097.75 | 17097.75 | INR Seventeen Thousand &Ninety Seven and Paise Seventy Five Only | 3.96 | Mini- trunking |  | 75 | Mtr.
3.97 | End cap left or right |  | 8 | Nos. | 141.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1129.36 | 1129.36 | INR One Thousand One Hundred & Twenty Nine and Paise Thirty Six Only | 3.97 | End cap left or right |  | 8 | Nos.
3.98 | Internal/ external angle |  | 16 | Nos. | 145.55 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2328.8 | 2328.8 | INR Two Thousand Three Hundred & Twenty Eight and Paise Eighty Only | 3.98 | Internal/ external angle |  | 16 | Nos.
3.99 | Flat angle |  | 17 | Nos. | 123.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2101.71 | 2101.71 | INR Two Thousand One Hundred & One and Paise Seventy One Only | 3.99 | Flat angle |  | 17 | Nos.
4 | Flat junction |  | 6 | Nos. | 143.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 862.8 | 862.8 | INR Eight Hundred & Sixty Two and Paise Eighty Only | 4 | Flat junction |  | 6 | Nos.
4.01 | S & Laying of one no. XLPE cable aluminum conductor steel armoured power cable of 1.1kV grade of size 3-1/2x70 sq.mm. in following manners. | [53 empty] | 4.01 | S & Laying of one no. XLPE cable aluminum conductor steel armoured power cable of 1.1kV grade of size 3-1/2x70 sq.mm. in following manners.
4.02 | In open duct |  | 5 | Mtr | 445.42 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2227.1 | 2227.1 | INR Two Thousand Two Hundred & Twenty Seven and Paise Ten Only | 4.02 | In open duct |  | 5 | Mtr
4.03 | On surface with MS clamp |  | 30 | Mtr | 508.55 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15256.5 | 15256.5 | INR Fifteen Thousand Two Hundred & Fifty Six and Paise Fifty Only | 4.03 | On surface with MS clamp |  | 30 | Mtr
4.04 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor. | [53 empty] | 4.04 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor.
4.05 | 10,16 mm |  | 48 | Nos. | 35.07 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1683.36 | 1683.36 | INR One Thousand Six Hundred & Eighty Three and Paise Thirty Six Only | 4.05 | 10,16 mm |  | 48 | Nos.
4.06 | 35 mm |  | 8 | Nos. | 46.47 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 371.76 | 371.76 | INR Three Hundred & Seventy One and Paise Seventy Six Only | 4.06 | 35 mm |  | 8 | Nos.
4.07 | Dismentaling and refixing of light fittings of any sizess on surface or in recessed etc as reqd. |  | 4 | Nos. | 222.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 890.84 | 890.84 | INR Eight Hundred & Ninety and Paise Eighty Four Only | 4.07 | Dismentaling and refixing of light fittings of any sizess on surface or in recessed etc as reqd. |  | 4 | Nos.
4.08 | Dismantling & refixing of any size fan with fasner from normal height | [53 empty] | 4.08 | Dismantling & refixing of any size fan with fasner from normal height
4.09 | ceiling fan |  | 2 | Nos. | 222.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 445.42 | 445.42 | INR Four Hundred & Forty Five and Paise Forty Two Only | 4.09 | ceiling fan |  | 2 | Nos.
4.1 | Supplying and fixing of following modular switch/sockets on the existing Clip-on 85mm cover of 105mmx50mm DLP plastic trunking including connection etc as required complete of approved make ( Arteor model of Legrand or equivalent). | [53 empty] | 4.1 | Supplying and fixing of following modular switch/sockets on the existing Clip-on 85mm cover of 105mmx50mm DLP plastic trunking including connection etc as required complete of approved make ( Arteor model of Legrand or equivalent).
4.11 | 6 Amp switch |  | 110 | Nos. | 239.37 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 26330.7 | 26330.7 | INR Twenty Six Thousand Three Hundred & Thirty and Paise Seventy Only | 4.11 | 6 Amp switch |  | 110 | Nos.
4.12 | 20 Amp. switch |  | 94 | Nos. | 426.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 40056.22 | 40056.22 | INR Forty Thousand &Fifty Six and Paise Twenty Two Only | 4.12 | 20 Amp. switch |  | 94 | Nos.
4.13 | 6 Amp. 2/3 pin socket outlet |  | 98 | Nos. | 279.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 27410.6 | 27410.6 | INR Twenty Seven Thousand Four Hundred & Ten and Paise Sixty Only | 4.13 | 6 Amp. 2/3 pin socket outlet |  | 98 | Nos.
4.14 | 6/16 Amp. three pin two module socket outlet. |  | 94 | Nos. | 546.25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 51347.5 | 51347.5 | INR Fifty One Thousand Three Hundred & Forty Seven and Paise Fifty Only | 4.14 | 6/16 Amp. three pin two module socket outlet. |  | 94 | Nos.
4.15 | S & F metal enclosure suitable for DP/TPN /FP MCB / DP ELCB on surface or recessed etc as reqd. |  | 13 | Nos. | 906.62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11786.06 | 11786.06 | INR Eleven Thousand Seven Hundred & Eighty Six and Paise Six Only | 4.15 | S & F metal enclosure suitable for DP/TPN /FP MCB / DP ELCB on surface or recessed etc as reqd. |  | 13 | Nos.
4.16 | Laying UTP cable enhanced cat 5/cat 6 cable in existing steel conduit pipe/GI pipe/ raceway / RCC pipe as reqd. the cost shall also include numbering of networking wire from room to rack as reqd. (wire will be supplied by dept) |  | 1110 | Mtr. | 18.41 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 20435.1 | 20435.1 | INR Twenty Thousand Four Hundred & Thirty Five and Paise Ten Only | 4.16 | Laying UTP cable enhanced cat 5/cat 6 cable in existing steel conduit pipe/GI pipe/ raceway / RCC pipe as reqd. the cost shall also include numbering of networking wire from room to rack as reqd. (wire will be supplied by dept) |  | 1110 | Mtr.
4.17 | Fixing of RJ-45 modular box with cover plate or I/o box for internet on surface/ recessed cutting the wall making good the same as required. ( box and cover plate will be supplied by dept.) |  | 40 | Nos. | 77.16 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3086.4 | 3086.4 | INR Three Thousand &Eighty Six and Paise Forty Only | 4.17 | Fixing of RJ-45 modular box with cover plate or I/o box for internet on surface/ recessed cutting the wall making good the same as required. ( box and cover plate will be supplied by dept.) |  | 40 | Nos.
4.18 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable Gl box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. | [53 empty] | 4.18 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable Gl box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required.
4.19 | Group C |  | 5 | Point | 1617.71 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8088.55 | 8088.55 | INR Eight Thousand &Eighty Eight and Paise Fifty Five Only | 4.19 | Group C |  | 5 | Point
4.2 | Rewiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel/PVC conduit including dismantling as required. | [53 empty] | 4.2 | Rewiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel/PVC conduit including dismantling as required.
4.21 | Group C |  | 48 | Point | 783.87 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 37625.76 | 37625.76 | INR Thirty Seven Thousand Six Hundred & Twenty Five and Paise Seventy Six Only | 4.21 | Group C |  | 48 | Point
4.22 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. | [53 empty] | 4.22 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
4.23 | 20 mm |  | 20 | Metre | 195.53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3910.6 | 3910.6 | INR Three Thousand Nine Hundred & Ten and Paise Sixty Only | 4.23 | 20 mm |  | 20 | Metre
4.24 | Supplying, installation of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mm x 50mm etc. as reqd. | [53 empty] | 4.24 | Supplying, installation of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mm x 50mm etc. as reqd.
4.25 | 3 module |  | 48 | Nos. | 300.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14436 | 14436 | INR Fourteen Thousand Four Hundred & Thirty Six Only | 4.25 | 3 module |  | 48 | Nos.
4.26 | Chemical Earthing with GI earth electrode 50 mm dia x 3 Mtr length with full GI strip including earth enhancing compound and RCC precast PIT cover and earthing pit etc as reqd. |  | 6 | No. | 7051.29 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 42307.74 | 42307.74 | INR Forty Two Thousand Three Hundred & Seven and Paise Seventy Four Only | 4.26 | Chemical Earthing with GI earth electrode 50 mm dia x 3 Mtr length with full GI strip including earth enhancing compound and RCC precast PIT cover and earthing pit etc as reqd. |  | 6 | No.
4.27 | S & F following size of steel flexible pipe along with the accessories on surface etc as required | [53 empty] | 4.27 | S & F following size of steel flexible pipe along with the accessories on surface etc as required
4.28 | 25 mm |  | 5 | Meter | 71.02 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 355.1 | 355.1 | INR Three Hundred & Fifty Five and Paise Ten Only | 4.28 | 25 mm |  | 5 | Meter
4.29 | 32 mm |  | 5 | Meter | 83.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 416.5 | 416.5 | INR Four Hundred & Sixteen and Paise Fifty Only | 4.29 | 32 mm |  | 5 | Meter
4.3 | Providing and fixing 25 mm X 5 mm G.l. strip on surface or in recess for connections etc. as required. |  | 85 | Metre | 213.94 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 18184.9 | 18184.9 | INR Eighteen Thousand One Hundred & Eighty Four and Paise Ninety Only | 4.3 | Providing and fixing 25 mm X 5 mm G.l. strip on surface or in recess for connections etc. as required. |  | 85 | Metre
4.31 | Supply and fixing of following LED light fixture with efficiency >100 lumen/ watt, P.F. >0.95, THD<10%, Electronic driver, LED lamp, reflector, diffuser, MS body/housing holder etc. complete with all fixing accessories and lamp as required complete. | [53 empty] | 4.31 | Supply and fixing of following LED light fixture with efficiency >100 lumen/ watt, P.F. >0.95, THD<10%, Electronic driver, LED lamp, reflector, diffuser, MS body/housing holder etc. complete with all fixing accessories and lamp as required complete.
4.32 | 1 X 20W Box type LED tube with fitting |  | 3 | Nos. | 817.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2451.57 | 2451.57 | INR Two Thousand Four Hundred & Fifty One and Paise Fifty Seven Only | 4.32 | 1 X 20W Box type LED tube with fitting |  | 3 | Nos.
4.33 | 36 watt surface mounting LED light fixture 300 x 1200 mm |  | 12 | Nos. | 5991.23 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 71894.76 | 71894.76 | INR Seventy One Thousand Eight Hundred & Ninety Four and Paise Seventy Six Only | 4.33 | 36 watt surface mounting LED light fixture 300 x 1200 mm |  | 12 | Nos.
4.34 | Supplying and fixing following size/ modules, Gl box alongwith modular base & cover plate for modular switches in recess etc. as required. | [53 empty] | 4.34 | Supplying and fixing following size/ modules, Gl box alongwith modular base & cover plate for modular switches in recess etc. as required.
4.35 | 6 Module (200mmX75mm) |  | 1 | No. | 352.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 352.48 | 352.48 | INR Three Hundred & Fifty Two and Paise Forty Eight Only | 4.35 | 6 Module (200mmX75mm) |  | 1 | No.
4.36 | 12 Module (200mmX150mm) |  | 1 | No. | 479.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 479.61 | 479.61 | INR Four Hundred & Seventy Nine and Paise Sixty One Only | 4.36 | 12 Module (200mmX150mm) |  | 1 | No.
4.37 | Supplying and fixing connecting and commissioning following rating, Four pole, 35kA MCCB with microprocessor based LS-I release in the existing DB/ Box as required complete. | [53 empty] | 4.37 | Supplying and fixing connecting and commissioning following rating, Four pole, 35kA MCCB with microprocessor based LS-I release in the existing DB/ Box as required complete.
4.38 | 160 A |  | 2 | Nos. | 35064.45 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 70128.9 | 70128.9 | INR Seventy Thousand One Hundred & Twenty Eight and Paise Ninety Only | 4.38 | 160 A |  | 2 | Nos.
4.39 | Supplying and fixing exhaust fan shutter for following sizes exhaust fan on rag bolts as reqd complete. | [53 empty] | 4.39 | Supplying and fixing exhaust fan shutter for following sizes exhaust fan on rag bolts as reqd complete.
4.4 | for 300 mm / 12" sweep |  | 1 | Nos. | 775.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 775.98 | 775.98 | INR Seven Hundred & Seventy Five and Paise Ninety Eight Only | 4.4 | for 300 mm / 12" sweep |  | 1 | Nos.
4.41 | for 450 mm / 18" sweep |  | 2 | Nos. | 964.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1928.98 | 1928.98 | INR One Thousand Nine Hundred & Twenty Eight and Paise Ninety Eight Only | 4.41 | for 450 mm / 18" sweep |  | 2 | Nos.
4.42 | Supply, Installation testing and commissioning of following seep, copper wound, 900 RPM, 220 volt AC, 50 Hz exhaust fan in the existing opening etc as required complete. | [53 empty] | 4.42 | Supply, Installation testing and commissioning of following seep, copper wound, 900 RPM, 220 volt AC, 50 Hz exhaust fan in the existing opening etc as required complete.
4.43 | 300 mm / 12" sweep |  | 1 | Nos. | 3755.37 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3755.37 | 3755.37 | INR Three Thousand Seven Hundred & Fifty Five and Paise Thirty Seven Only | 4.43 | 300 mm / 12" sweep |  | 1 | Nos.
4.44 | 450 mm / 18" sweep |  | 2 | Nos. | 5789.57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11579.14 | 11579.14 | INR Eleven Thousand Five Hundred & Seventy Nine and Paise Fourteen Only | 4.44 | 450 mm / 18" sweep |  | 2 | Nos.
4.45 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, incomer TPN MCCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.) | [53 empty] | 4.45 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, incomer TPN MCCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
4.46 | 12 way , Double door |  | 1 | No. | 29007.45 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 29007.45 | 29007.45 | INR Twenty Nine Thousand &Seven and Paise Forty Five Only | 4.46 | 12 way , Double door |  | 1 | No.
4.47 | Dismantling, disconnecting old damaged unserviceable fl fitting/ exhaust fan/ ceiling fan/ bulkhead fitting with bracket etc. as reqd. and depositing in sectional store. |  | 47 | Nos. | 94.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4450.9 | 4450.9 | INR Four Thousand Four Hundred & Fifty and Paise Ninety Only | 4.47 | Dismantling, disconnecting old damaged unserviceable fl fitting/ exhaust fan/ ceiling fan/ bulkhead fitting with bracket etc. as reqd. and depositing in sectional store. |  | 47 | Nos.
4.48 | Dismantling concealed & damaged DB/TPN Switches/starter/ loose wire boxes along with all accessories and depositing the same in the sectional store repairing the damages as reqd complete. |  | 63 | Nos. | 241.12 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15190.56 | 15190.56 | INR Fifteen Thousand One Hundred & Ninety and Paise Fifty Six Only | 4.48 | Dismantling concealed & damaged DB/TPN Switches/starter/ loose wire boxes along with all accessories and depositing the same in the sectional store repairing the damages as reqd complete. |  | 63 | Nos.
4.49 | Dismantling the old conduit pipe/wood batten of all sizes from surface/recessed & making good the damages I/c filling the holes of the surface etc as reqd. and depositing it in sectional store. |  | 440 | Meter | 30.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 13503.6 | 13503.6 | INR Thirteen Thousand Five Hundred & Three and Paise Sixty Only | 4.49 | Dismantling the old conduit pipe/wood batten of all sizes from surface/recessed & making good the damages I/c filling the holes of the surface etc as reqd. and depositing it in sectional store. |  | 440 | Meter
4.5 | Fixing 20/25/32 mm conduit pipe/ DLP on surface with clamp/in recessed only conduit pipe supplied by department.(Free of cost) |  | 15 | Meter | 113.99 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1709.85 | 1709.85 | INR One Thousand Seven Hundred & Nine and Paise Eighty Five Only | 4.5 | Fixing 20/25/32 mm conduit pipe/ DLP on surface with clamp/in recessed only conduit pipe supplied by department.(Free of cost) |  | 15 | Meter
4.51 | S&F connecting and commissioning independent mounting of MCCB enclosure suitable for MCCB's up to 250A in surface/recess I/c cutting the wall and making good the same in case of recessed (Cat No CS-CNM0100021 C & S or approved equivalent make) as reqd. |  | 1 | Nos. | 3381.85 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3381.85 | 3381.85 | INR Three Thousand Three Hundred & Eighty One and Paise Eighty Five Only | 4.51 | S&F connecting and commissioning independent mounting of MCCB enclosure suitable for MCCB's up to 250A in surface/recess I/c cutting the wall and making good the same in case of recessed (Cat No CS-CNM0100021 C & S or approved equivalent make) as reqd. |  | 1 | Nos.
4.52 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.) | [53 empty] | 4.52 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
4.53 | 8 way (4 + 24), Double door |  | 2 | No. | 8912.76 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 17825.52 | 17825.52 | INR Seventeen Thousand Eight Hundred & Twenty Five and Paise Fifty Two Only | 4.53 | 8 way (4 + 24), Double door |  | 2 | No.
4.54 | 12 way (4 + 36), Double door |  | 1 | No. | 11252.08 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11252.08 | 11252.08 | INR Eleven Thousand Two Hundred & Fifty Two and Paise Eight Only | 4.54 | 12 way (4 + 36), Double door |  | 1 | No.
4.55 | Supply & Laying of 40 mm dia, 8Kg / cm², minimum 2.0 mm thick HDPE pipe, ISI mark in following manners as required complete. | [53 empty] | 4.55 | Supply & Laying of 40 mm dia, 8Kg / cm², minimum 2.0 mm thick HDPE pipe, ISI mark in following manners as required complete.
4.56 | in ground I/c excavation, sand cushioning, protective covering and refixing the trench etc as reqd |  | 15 | Meter | 521.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7825.5 | 7825.5 | INR Seven Thousand Eight Hundred & Twenty Five and Paise Fifty Only | 4.56 | in ground I/c excavation, sand cushioning, protective covering and refixing the trench etc as reqd |  | 15 | Meter
4.57 | On Surface |  | 3 | Meter | 264.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 794.4 | 794.4 | INR Seven Hundred & Ninety Four and Paise Forty Only | 4.57 | On Surface |  | 3 | Meter
4.58 | Supply and fixing of following LED light fixture with efficiency >100 lumen/ watt, P.F. >0.95, THD<10%, Electronic driver, LED lamp, reflector, diffuser, MS body/housing holder etc. complete with all fixing accessories and lamp as required complete. | [53 empty] | 4.58 | Supply and fixing of following LED light fixture with efficiency >100 lumen/ watt, P.F. >0.95, THD<10%, Electronic driver, LED lamp, reflector, diffuser, MS body/housing holder etc. complete with all fixing accessories and lamp as required complete.
4.59 | 36 watt surface mounting LED light fixture 600 x600 mm |  | 22 | Nos. | 5545.81 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 122007.82 | 122007.82 | INR One Lakh Twenty Two Thousand &Seven and Paise Eighty Two Only | 4.59 | 36 watt surface mounting LED light fixture 600 x600 mm |  | 22 | Nos.
4.6 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. |  | 6 | No. | 1421.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8527.86 | 8527.86 | INR Eight Thousand Five Hundred & Twenty Seven and Paise Eighty Six Only | 4.6 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. |  | 6 | No.
4.61 | Dismantling and refixing of M.S./PVC box of up to 250 x 300 x100 on surface recessed as required. including painting with enamel paint as reqd |  | 2 | Nos. | 346.34 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 692.68 | 692.68 | INR Six Hundred & Ninety Two and Paise Sixty Eight Only | 4.61 | Dismantling and refixing of M.S./PVC box of up to 250 x 300 x100 on surface recessed as required. including painting with enamel paint as reqd |  | 2 | Nos.
4.62 | Supplying, fixing, painting of 15mm dia GI heavy class pipe down rod for ceiling fan etc as required complete. |  | 8 | Meter | 266.55 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2132.4 | 2132.4 | INR Two Thousand One Hundred & Thirty Two and Paise Forty Only | 4.62 | Supplying, fixing, painting of 15mm dia GI heavy class pipe down rod for ceiling fan etc as required complete. |  | 8 | Meter
4.63 | Extra for cutting and drilling hole in down rod of 15mm dia GI pipe for ceiling fan etc. as required complete. |  | 8 | Nos. | 72.78 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 582.24 | 582.24 | INR Five Hundred & Eighty Two and Paise Twenty Four Only | 4.63 | Extra for cutting and drilling hole in down rod of 15mm dia GI pipe for ceiling fan etc. as required complete. |  | 8 | Nos.
4.64 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CM/M/W) minimum 6.00, Air delivery minimum 210 Cum/Min , 350 RPM (tolerance as per IS : 374-2019),THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase ACSupply, earthing etc. complete as required. |  | 8 | Nos. | 2393.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19149.52 | 19149.52 | INR Nineteen Thousand One Hundred & Forty Nine and Paise Fifty Two Only | 4.64 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CM/M/W) minimum 6.00, Air delivery minimum 210 Cum/Min , 350 RPM (tolerance as per IS : 374-2019),THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase ACSupply, earthing etc. complete as required. |  | 8 | Nos.
4.65 | Supplying and fixing following size/ modules, plastic box for modular switches in recess etc as required. | [53 empty] | 4.65 | Supplying and fixing following size/ modules, plastic box for modular switches in recess etc as required.
4.66 | 12 Module |  | 2 | Nos. | 823.32 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1646.64 | 1646.64 | INR One Thousand Six Hundred & Forty Six and Paise Sixty Four Only | 4.66 | 12 Module |  | 2 | Nos.
Total in Figures | [51 empty] | 3991395 | 3991395 | Thirty Nine Lakh Ninety One Thousand Three Hundred & Ninety Five Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Words |  | INR Zero Only
Note on K25: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K26: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K28: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K29: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.

## Macros
Please Enable Macros to View BoQ information