## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: Providing and making three phase and single phase power points at UG manufacturing lab at DJAC, IIT Kanpur
NIT No: Electrical/11/08/2023-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Component | [53 empty] | 1 | Component |  |  |  | 1 | Component
1.01 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. | item no.1 | [52 empty] | 1.01 | Supply installation testing and commissioning of cubical type LT panel-01 (IEC 61439 ) suitable for 4000Amp 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferable) design from CRCA sheet steel of 2mm thick for frame work and covers. 3mm thick for gland plated i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type FP Aluminium alloy Bus bars of high conductivity. DMC.SMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos earth solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant low smoke insulated copper conductor s/c cable, cable alleys, cable gland plate in two half. | item no.1 |  |  | 1.01 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. | item no.1
1.02 | 3 x 4 sq. mm | item no.2 | 135 | Metre | 180.62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 24384 | 24384 | INR Twenty Four Thousand Three Hundred & Eighty Four Only | 1.02 | The panel shall be equipped with relays, timers set of CT's for metering & protection and energy analyser/meter (on all incomer and outgoing feeders) to indicate current phase, line voltage, frequency, power factor, KWH, KVARH. Provision of over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications amended up to date complete. and attached specification. | item no.2 |  |  | 1.02 | 3 x 4 sq. mm | item no.2 | 135 | Metre
1.03 | 6 x 6 sq. mm | item no.3 | 125 | Metre | 524.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 65541 | 65541 | INR Sixty Five Thousand Five Hundred & Forty One Only | 1.03 | Incoming | item no.3 |  |  | 1.03 | 6 x 6 sq. mm | item no.3 | 125 | Metre
1.04 | 6 x 16 sq.mm. | item no.4 | 30 | Meter | 1523.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 45717 | 45717 | INR Forty Five Thousand Seven Hundred & Seventeen Only | 1.04 | 2 No's 4000A, FP, EDO,50KA, ACB with microprocessor release (O/L, S/C & E/F protention) saftey shutter,SCM, CC, 4NO+4NC Aux. Contacts, interlock, shunt Trip contact T&C. etc. suitable to connect with the bus duct and through cables. ABB-Emax2/ Schneider MTZ/Siemens 3VA | item no.4 |  |  | 1.04 | 6 x 16 sq.mm. | item no.4 | 30 | Meter
1.05 | Supply and fixing of 32 x 20 mm DLP mini- trunking white-system with independent cover etc. as required complete. | item no.5 | 30 | Meter | 227.97 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6839 | 6839 | INR Six Thousand Eight Hundred & Thirty Nine Only | 1.05 | breaker control switch TNC, Digital voltmeter/Ammeter Cl-1.0 with selector switch, Electronic KWH meter Cl-1.0, CT-4000/5A, Cl1.0, 15KVA cast rasin for metering, protection CTs 4000/5A, Cl-5P10, 15VA cast rasin IDMT relay , Trip circuit supervision relay , Phase indicating Lamp LED Type"Red, Tellow, Blue" Auto / Amnual selector switch Auxiliary contactors with 2NO+2NC , 2A SP MCB 10KA for cont. CKT. | item no.5 |  |  | 1.05 | Supply and fixing of 32 x 20 mm DLP mini- trunking white-system with independent cover etc. as required complete. | item no.5 | 30 | Meter
1.06 | Supply and fixing of following accessories suitable for 32 mm x 20 mm size plastic trunking white system. | item no.6 | [52 empty] | 1.06 | Both Incomer shall have class-b SPD of DEHN make. With 50KA 40A MPCB Protection. | item no.6 |  |  | 1.06 | Supply and fixing of following accessories suitable for 32 mm x 20 mm size plastic trunking white system. | item no.6
1.07 | End cap | item no.7 | 2 | Nos. | 150.81 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 302 | 302 | INR Three Hundred & Two Only | 1.07 | Bus bar: 1 No.4000 A, 50HZ, FP, Aliminium Bus Bar | item no.7 |  |  | 1.07 | End cap | item no.7 | 2 | Nos.
1.08 | internal / external angle | item no.8 | 2 | Nos. | 145.55 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 291 | 291 | INR Two Hundred & Ninety One Only | 1.08 | OutGoing: | item no.8 |  |  | 1.08 | internal / external angle | item no.8 | 2 | Nos.
1.09 | changeable flat angle | item no.9 | 4 | Nos. | 123.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 495 | 495 | INR Four Hundred & Ninety Five Only | 1.09 | 2 nos.2500 A, FP, EDO, 50 kA ACB with MPR based release (O/L, S/C & E/F protection) safety shutter, Aux. contacts 4NONC-2Nos, Breaker control switch TNC- 2Nos. 2A SP MCB 10KA for cont. CKT- 2nos. | item no.9 |  |  | 1.09 | changeable flat angle | item no.9 | 4 | Nos.
1.1 | flat junction | item no.10 | 1 | Nos. | 143.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 144 | 144 | INR One Hundred & Forty Four Only | 1.1 | 2 nos.1600 A, FP, EDO, 50 kA ACB with MPR based release (O/L, S/C & E/F protection) safety shutter, Aux. contacts 4NONC-2Nos, Breaker control switch TNC- 2Nos. 2A SP MCB 10KA for cont. CKT- 2nos. | item no.10 |  |  | 1.1 | flat junction | item no.10 | 1 | Nos.
1.11 | Supply and fixing of 105 x 50 mm DLP trunking white-system but without cover and partition etc. as required complete. | item no.11 | 60 | Meter | 979.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 58764 | 58764 | INR Fifty Eight Thousand Seven Hundred & Sixty Four Only | 1.11 | 3 nos. 800 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism-3Nos, FP Spreader(8x3=24Nos) for MCCB 800A- 3 Nos | item no.11 |  |  | 1.11 | Supply and fixing of 105 x 50 mm DLP trunking white-system but without cover and partition etc. as required complete. | item no.11 | 60 | Meter
1.12 | Supply and fixing of following accessories suitable for 105 mm x 50 mm size plastic trunking white system. | item no.12 | [52 empty] | 1.12 | 2 nos. 630 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism-2Nos, FP Spreader(8x2=16Nos) for MCCB 630A- 2Nos | item no.12 |  |  | 1.12 | Supply and fixing of following accessories suitable for 105 mm x 50 mm size plastic trunking white system. | item no.12
1.13 | 85 mm flexible cover | item no.13 | 58 | Meter | 432.27 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 25072 | 25072 | INR Twenty Five Thousand &Seventy Two Only | 1.13 | 4 nos. 400 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism-4Nos, FP Spreader(8x4=32Nos) for MCCB 400A- 4 Nos | item no.13 |  |  | 1.13 | 85 mm flexible cover | item no.13 | 58 | Meter
1.14 | End cap | item no.14 | 6 | Nos. | 194.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1168 | 1168 | INR One Thousand One Hundred & Sixty Eight Only | 1.14 | all out goings with ON.OFF, Trip, Spring charge indication.communicable type Digital multifunction energy meter(RS 485).Digital Amp meter with selector switches etc. | item no.14 |  |  | 1.14 | End cap | item no.14 | 6 | Nos.
1.15 | Internal angles- adjustable from 80°-100° | item no.15 | 4 | Nos. | 539.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2157 | 2157 | INR Two Thousand One Hundred & Fifty Seven Only | 1.15 | Note : All ACBs and MCCB's aux. contacts for ON/OFF and trip spare contacts to be wired up to terminal block. | item no.15 | 1 | No. | 1.15 | Internal angles- adjustable from 80°-100° | item no.15 | 4 | Nos.
1.16 | external angles- adjustable from 60°-120° | item no.16 | 2 | Nos. | 550.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1101 | 1101 | INR One Thousand One Hundred & One Only | 1.16 | Supply installation testing and commissioning of cubical type DG set LT panel -2 (IEC 61439), suitable for 1600 Amp 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferable) design from CRCA sheet steel of 2mm thick for frame work and covers. 3mm thick for gland plated i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type FP Aluminium alloy Bus bars of high conductivity. DMC.SMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos earth solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant low smoke insulated copper conductor s/c cable, cable alleys, cable gland plate in two half. | item no.16 |  |  | 1.16 | external angles- adjustable from 60°-120° | item no.16 | 2 | Nos.
1.17 | flat junction | item no.17 | 2 | Nos. | 938.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1876 | 1876 | INR One Thousand Eight Hundred & Seventy Six Only | 1.17 | The panel shall be equipped with relays, timers set of CT's for metering & protection and energy analyser/meter to indicate current phase, line voltage, frequency, power factor, KWH, KVARH. Provision of over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications amended up to date complete. and attached specification. | item no.17 |  |  | 1.17 | flat junction | item no.17 | 2 | Nos.
1.18 | flat angles | item no.18 | 3 | Nos. | 762.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2288 | 2288 | INR Two Thousand Two Hundred & Eighty Eight Only | 1.18 | Incoming | item no.18 |  |  | 1.18 | flat angles | item no.18 | 3 | Nos.
1.19 | separation partitions | item no.19 | 20 | Meter | 260.41 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5208 | 5208 | INR Five Thousand Two Hundred & Eight Only | 1.19 | 3 No's 1250A, FP, 50KA, 4 pole ACB ( for 3x750 KVA SG sets) with microprocessor release (O/L, S/C & E/F protention) saftey shutter,SCM, CC, 4NO+4NC Aux. Contacts, interlock, shunt Trip contact T&C. etc. with 2 nos. 1250 A bus coupler (DG1 & DG2) (DG2-DG3) with all protections and metering. | item no.19 |  |  | 1.19 | separation partitions | item no.19 | 20 | Meter
1.2 | Joints for 85mm width cover | item no.20 | 25 | Nos. | 224.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5612 | 5612 | INR Five Thousand Six Hundred & Twelve Only | 1.2 | breaker control switch TNC, Digital voltmeter/Ammeter Cl-1.0 with selector switch, Electronic KWH meter Cl-1.0, CT-1250/5A, Cl1.0, 15VA cast rasin for metering, protection CTs 1250/5A, Cl-5P10, 15VA cast rasin IDMT relay , Trip circuit supervision relay , Phase indicating Lamp LED Type"Red, Tellow, Blue" Auto / Amnual selector switch Auxiliary contactors with 2NO+2NC , 2A SP MCB 10KA for cont. CKT. | item no.20 |  |  | 1.2 | Joints for 85mm width cover | item no.20 | 25 | Nos.
1.21 | base joints | item no.21 | 50 | Nos. | 90.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4516 | 4516 | INR Four Thousand Five Hundred & Sixteen Only | 1.21 | All the Incomer shall have class-b SPD of DEHN make. With 50KA 40A MPCB Protection. | item no.21 |  |  | 1.21 | base joints | item no.21 | 50 | Nos.
1.22 | Supplying, installation of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mm x 50mm etc. as reqd. | item no.22 | [52 empty] | 1.22 | Bus bar: 1 No.1600 A, 50HZ, FP, Aliminium Bus Bar | item no.22 |  |  | 1.22 | Supplying, installation of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mm x 50mm etc. as reqd. | item no.22
1.23 | 3 module | item no.23 | 8 | Nos. | 300.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2406 | 2406 | INR Two Thousand Four Hundred & Six Only | 1.23 | OutGoing: | item no.23 |  |  | 1.23 | 3 module | item no.23 | 8 | Nos.
1.24 | 6 module | item no.24 | 4 | Nos. | 403.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1613 | 1613 | INR One Thousand Six Hundred & Thirteen Only | 1.24 | 3 nos. 800 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism- 3Nos, 2A SP MCB for cont. CKT.- 3 Nos | item no.24 |  |  | 1.24 | 6 module | item no.24 | 4 | Nos.
1.25 | S & F following size of steel flexible pipe along with the accessories on surface etc as required | item no.25 | [52 empty] | 1.25 | 8 nos. 400 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism- 8Nos, 2A SP MCB for cont. CKT.- 8 Nos | item no.25 |  |  | 1.25 | S & F following size of steel flexible pipe along with the accessories on surface etc as required | item no.25
1.26 | 32 mm | item no.26 | 15 | Meter | 83.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1250 | 1250 | INR One Thousand Two Hundred & Fifty Only | 1.26 | 4 nos. 250 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection - 3nos, rotary operated handle mechanism-4Nos, FP Spreader for MCCB 250A- 4 Nos | item no.26 |  |  | 1.26 | 32 mm | item no.26 | 15 | Meter
1.27 | Supplying and fixing following rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | item no.27 | [52 empty] | 1.27 | all outgoings with ON,OFF,Trip, spring charge indication. Communicable Digital multifunction energy meter(RS 485) . Digital Amp meter with selector switches etc. | item no.27 |  |  | 1.27 | Supplying and fixing following rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | item no.27
1.28 | Single pole 5 A to 32 A | item no.28 | 6 | No. | 224.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1347 | 1347 | INR One Thousand Three Hundred & Forty Seven Only | 1.28 | Note : All ACBs and MCCB's aux. contacts for ON/OFF and trip spare contacts to be wired up to terminal block. | item no.28 | 1 | Nos. | 1.28 | Single pole 5 A to 32 A | item no.28 | 6 | No.
1.29 | Triple pole 5 A to 32 A | item no.29 | 6 | No. | 882.95 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5298 | 5298 | INR Five Thousand Two Hundred & Ninety Eight Only | 1.29 | S&I, testing & commissioning 4000 amp TPN aluminum bus duct with MS enclosure, as pe r enclosed specifications E-02. | item no.29 | 15 | Mtr. | 1.29 | Triple pole 5 A to 32 A | item no.29 | 6 | No.
1.3 | Triple pole and neutral 5 A to 32 A | item no.30 | 5 | No. | 1076.72 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5384 | 5384 | INR Five Thousand Three Hundred & Eighty Four Only | 1.3 | S&I, testing & commissioning 4000amp TPN copper flexible links to connect tranformer LT bus duct as per enclosed specifications E-02. | item no.30 | 1 | Set | 1.3 | Triple pole and neutral 5 A to 32 A | item no.30 | 5 | No.
1.31 | Single Pole (40A-63A) | item no.31 | 3 | Nos. | 719.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2160 | 2160 | INR Two Thousand One Hundred & Sixty Only | 1.31 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | item no.31 | 5 | Nos. | 1.31 | Single Pole (40A-63A) | item no.31 | 3 | Nos.
1.32 | Triple pole (40A-63A) | item no.32 | 3 | Nos. | 2427.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7281 | 7281 | INR Seven Thousand Two Hundred & Eighty One Only | 1.32 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | item no.32 | 100 | Mtr. | 1.32 | Triple pole (40A-63A) | item no.32 | 3 | Nos.
1.33 | Four Pole (40A-63A) | item no.33 | 2 | Nos. | 3037.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6075 | 6075 | INR Six Thousand &Seventy Five Only | 1.33 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | item no.33 |  |  | 1.33 | Four Pole (40A-63A) | item no.33 | 2 | Nos.
1.34 | S & F metal enclosure suitable for DP/TPN MCB / DP ELCB on surface or recessed etc as reqd. | item no.34 | 6 | Nos. | 906.62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5440 | 5440 | INR Five Thousand Four Hundred & Forty Only | 1.34 | 3½ X 400 sq. mm (82mm) | item no.34 | 50 | Nos. | 1.34 | S & F metal enclosure suitable for DP/TPN MCB / DP ELCB on surface or recessed etc as reqd. | item no.34 | 6 | Nos.
1.35 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.) | item no.35 | [52 empty] | 1.35 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | item no.35 |  |  | 1.35 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.) | item no.35
1.36 | 12 way (4 + 36), Double door | item no.36 | 1 | No. | 11252.08 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11252 | 11252 | INR Eleven Thousand Two Hundred & Fifty Two Only | 1.36 | 3½ X 300 sq. mm | item no.36 | 4 | Nos. | 1.36 | 12 way (4 + 36), Double door | item no.36 | 1 | No.
1.37 | Supplying and fixing following modular switch/ socket on the existing clip-on frame fixed on 85mm cover of 105 x 50 mm DLP plastic trunking including connections etc. as required complete. | item no.37 | [52 empty] | 1.37 | 3½ X 400 sq. mm | item no.37 | 4 | Nos. | 1.37 | Supplying and fixing following modular switch/ socket on the existing clip-on frame fixed on 85mm cover of 105 x 50 mm DLP plastic trunking including connections etc. as required complete. | item no.37
1.38 | 20 A switch | item no.38 | 16 | No. | 426.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6818 | 6818 | INR Six Thousand Eight Hundred & Eighteen Only | 1.38 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc. as required | item no.38 |  |  | 1.38 | 20 A switch | item no.38 | 16 | No.
1.39 | 6/16 A 3 pin socket outlet | item no.39 | 16 | No. | 546.25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8740 | 8740 | INR Eight Thousand Seven Hundred & Forty Only | 1.39 | 100 mm Dia | item no.39 | 50 | Mtr. | 1.39 | 6/16 A 3 pin socket outlet | item no.39 | 16 | No.
1.4 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor. | item no.40 | [52 empty] | 1.4 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels | item no.40 | 2 | Cum | 1.4 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor. | item no.40
1.41 | 6 /10/16 Sq.mm. | item no.41 | 12 | Nos. | 32.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 389 | 389 | INR Three Hundred & Eighty Nine Only | 1.41 | Providing 15 mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels. | item no.41 | 5 | Sqm | 1.41 | 6 /10/16 Sq.mm. | item no.41 | 12 | Nos.
Total in Figures |  |  |  | Nos. | [47 empty] | 316928 | 292544 | Two Lakh Ninety Two Thousand Five Hundred & Forty Four Only | [5 empty] | Total in Figures |  | 29911889
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only | [5 empty] | Quoted Rate in Figures |  | Excess (+)
Quoted Rate in Words | [59 empty] | Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information