## BOQ
BILL OF QUANTITY
Subject :-Rejuvenation of old Central AC (FCU's) system with double skin CS 2400 cfm AHU and floor/wall-mounted FCU's for energy efficient and comfort cooling at WL-110.
Name of Agency
S.No | Description | Qty | Unit | Rate | Amount
1 | SITC of double skin Horrizontal type Ceiling suspended air handling units (AHU) of panels consisting of pre coated G.I.casing of thickness 0.6 mm outside layer and 0.6 mm inside layer with 25 mm thick injected PUF of density not less than 40 Kg/CuM and i/c 25 mm thick Open cell nitrile/fiber glass insulation injected between intermediate & inner skin & tissue paper insulation with 0.8 mm perforated Al./GI inner sheet. The air handling units shall be complete with mixing chamber box with manually supply & fresh air aluminium damper, Filter-section with 50 mm thick boxs type synthetic fiber washable pre filter's section (90% down to 10 microns), coil section with 6 Rows Deep chilled water cooper coil & aluminium fins construction, fan section complete with forward curved DIDW centrifugal fan, V-belts, drive package, VFD compatible variable speed squirrel cage induction motor, Motor shall be suitable for 415±10% volts, 50 Hz, 3phase AC supply having fire retardent flexible connection, 20 G SS-304 stainless steel drain pan and vibration isolator all complete as per standerd specification. AHU shall be selected for a maximum face velocity of 500 FPM (2.5 MPS), Fan outlet velocity shall not exceed 1800 FPM (9.1 m/s)
a) | 2400 cfm, 6 Rows, static pressure 40, Ceiling suspended AHU with mixing chamber | 1 | Nos. |  | 0
2 | SITC of variable frequency drive (VFD) of model no.FC-102/Equvilant, with IP20, H2 RFI filter,Lcp of make Danfoss/equivalent & Resistive Tempearature Device (RTD) Make- Omricon/equvilant along with necessary Control/communication wiring in flexible condute for maximum energy conservation with following specifications complete as required. |  |  |  | 0
a) | 1.5 Kw | 1 | Nos. |  | 0
3 | SITC of modular type Fan Coil Unit (floor/wall-mounted) , The unit shall be complete with grills, insulated enclosure, drain tray, comprising of blower, 2/3 speed fan motor, 2/3 row copper coil section, washable filter section, 2 way motorised valve with actuator, and brass flair fitting for copper pipe connection, i/c all necessary support /hangers, vibration isolators etc. complete as reqd. |  |  |  | 0
a) | 2.0 TR nominal or higher capacity | 2 | No. |  | 0
b) | 2.25 TR nominal or higher capacity | 1 | No. |  | 0
4 | Providing and fixing Digital controler (Thermostate) corded in fan coil units of up to 3.5 TR Capacity re-commissioning i/c dismantling old if any etc. complete as reqd. | 3 | No. |  | 0
5 | Cutting & Dismantling of condensor / chilled water pipe line of following size for drain out the water from supply & return pipe line and making good i/c re-filling of water in pipe line ,testing & commissioning complete as required. |  |  |  | 0
a) | Up to 200 mm dia | 1 | Job |  | 0
6 | Supply, laying /fixing, testing and commissioning of MS Heavy 'C' class pipe ( IS :1239) of following sizes for chilled/ condenser water piping on surface / underground ( including fabrication of bends / elbows, tees, reducers, sockets, unions etc) with wooden / Puff block, masonry support / MS angle-clamp two coats primer/ enamel paint, vibration isolators and fittings as per standard specification complete as required. |  |  |  | 0
a) | 25 mm | 12 | Mtr |  | 0
b) | 32 mm | 10 | Mtr |  | 0
c) | 40 mm | 4 | Mtr |  | 0
d) | 50 mm | 44 | Mtr |  | 0
7 | Supplying & fixing insulation on existing MS 'C' class pipe over exposed surface/underground of following sizes with 50 mm thick fire retardant thermocole ( polystyrene) moulded pipe section of density 20 kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) , 500g polythene faced hessian cloth, wiremesh, sand-cement plaster & painting two or more coat to give even shade after applying one coat of ordinary paint etc complete as required. (Note:- Thermocole density should not be less than 20 kg/cu.m) |  |  |  | 0
a) | 32 mm | 10 | Mtr |  | 0
b) | 40 mm | 4 | Mtr |  | 0
c) | 50 mm | 44 | Mtr |  | 0
d) | 65 mm | 1 | Mtr |  | 0
8 | Supplying & fixing, insulation on existing pipe overhead/underground of following sizes with 19 mm thick Aluminium faced Nitrile rubber / closed sell expended polyethylene foam pipe section fixing with dendrite and tightening of insulation section PVC tape to be wrapped all around the joints. along with wrapping of tar felt peripheral of insulation etc complete as required. |  |  |  | 0
a) | 25 mm | 12 | Mtr |  | 0
9 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. |  |  |  | 0
a) | 0.63 mm (24 G) thick | 190 | SqM |  | 0
b) | 0.80 mm (22 G) thick | 20 | SqM |  | 0
10 | Supply and fixing of acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m³, with 25 mm X 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with Reinforced Plastic tissue paper and 0.5 mm thick perforated aluminium sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins, CPRX compound etc. complete as required and as per specifications. | 30 | SqM |  | 0
11 | Providing & fixing of thermal insulation with aluminium foil faced XLPE Class 'O' insulation sheet of following thickness on existing surface of duct with dendrite/adhesive and tightning with packing strip & lock at approx every 1.0 mtr distance etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminium tape complete as required. |  |  |  | 0
a) | 13 mm | 220 | SqM |  | 0
12 | Supplying and fixing testing and commissioning of Stainless steel ball valve size as mentioned below ISI marked with socket and nipple for drain line as per standard specifications. |  |  |  | 0
a) | 25 mm | 2 | Nos |  | 0
13 | Providing & fixing of Brass ball valve of following size with compatible to proportioning Copper/MS pipe i/c all necessary accessories, support /hangers, including old dismantling if any complete as reqd. |  |  |  | 0
a) | 20 mm | 2 | Nos |  | 0
b) | 25 mm | 1 | Nos |  | 0
14 | Providing & fixing of Brass Ball valve with Y-strainer of following size with compatible to proportioning Copper/MS pipe i/c all necessary support /hangers & dismantling old if any complete as reqd. |  |  |  | 0
a) | 20 mm | 2 | Nos |  | 0
b) | 25 mm | 1 | Nos |  | 0
15 | SITC of Butterfly valves CI body with SS Disc Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water with hand lever operated including nut, bolt, flanges, gasket as kind of existing pipe, painting with enamel including dismantling etc. complete as reqd. |  |  |  | 0
a) | 40 mm | 4 | Nos |  | 0
16 | Supplying & fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers as per specifications. | 1 | SqM |  | 0
17 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with lowers but without aluminium volume control dampers as reqd | 1 | SqM |  | 0
18 | Supply & fixing of fire retardant double cloth canvass made (up to 300 mm vide) with heavy clothes and suitable frame with G.I washer, nuts & bolts in suitable size. i/c jointing both sides with suitable gaskets complete as reqd. | 2 | Job |  | 0
19 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall |  |  |  | 0
a) | 25 mm nominal outer dia pipes | 15 | Mtr |  | 0
b) | 32 mm nominal outer dia pipes | 15 | Mtr |  | 0
20 | P & F ,testing and commissioning Three Phase DOL Starter suitable for Motor upto 5.0 HP / 3.75 kW, Amp range upto 9.3 A max, built in powder coated MS Box enclosure with Start - Stop push buttons etc complete as required. (Model- IHADOAJ1 Make Havells /Equvilant). | 1 | Nos. |  | 0
21 | Providing, laying, testing, and commissioning of following size Un-armoured PVC insulated Copper conducter power/controle cable of following size on surface/recessed complete as required. |  |  |  | 0
a) | 3 Core x 1.5 Sqmm, flexible Un-armoured copper cable | 8 | Mtr |  | 0
b) | 4 Core x 4.0 Sqmm, flexible Un-armoured copper cable | 15 | Mtr |  | 0
22 | Providing and fixing of 3 pin- 6 Amp. Single Phase Plug top ISI Marked for AC (FCU) unit complete as required. (Make:- Anchor or Equvilant) |  |  |  | 0
a) | 6 Amp | 2 | Nos |  | 0
23 | Supply and fixing UPVC mini trunking (casing-caping) & flexible conduit of following size white-system with independent cover- without central partion etc. as reqd |  |  |  | 0
a) | UPVC trunking 20mm x 12mm | 15 | Mtr |  | 0
b) | Flexi Conduit 20 mm | 8 | Mtr |  | 0
24 | Providing,laying & fixing of rainforced fiber flexible/soft PVC pipe of size given below etc. complete as reqd. |  |  |  | 0
a) | 20 mm | 2 | Mtr |  | 0
25 | Supply & fixing of copper piping 5/8" or 6/8" with 19 mm thick Class "O" Nitrile insulation on surface / recessed with flair nut, clamps etc. complete as reqd. | 6 | Mtr |  | 0
26 | Dismantling of Fan coil unit of Hi-wall/wall/floor mounted or ceiling suspended type up to 3.5 TR capacity including filter and valves etc. Complete as required. | 11 | Nos |  | 0
27 | Demolishing brick work i/c stacking of serviceable mat. with in 50 mtrs lead. In cement mortar | 0.5 | CuM |  | 0
28 | Making wall opening upto 600mm dia in any type / thick of wall and re-closing the opening with brick, sand, cement and plaster upto 20 mm i/c re-painting as per existing desigine/shape complete as required. | 3 | Job |  | 0
| Sub Total-A |  |  |  | 0
29 | Buy back cost of existing exposed/underground Old damage & rusted MS pipe with associated parts and taken away from site i/c cutting, dismentling,cartage etc Complete as required. |  |  |  | 0
a) | 25 mm | 15 | Mtr |  | 0
b) | 32 mm | 10 | Mtr |  | 0
30 | Buy back cost of existing any type FCU upto 2.0 tr capacity with associated parts and taken away from site Complete as required. | 11 | Nos |  | 0
| Sub Total-B |  |  |  | 0
| Sub Total (A-B) |  |  |  | 0