## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer
Name of Work: Construction of new 11kV/0.433 kV substation with 2x2500KVA transformers near SS No.9 for cater upcoming loads of NSM data Centre extension at IIT Kanpur (SH:Electrical works)
Contract No: 01/EE/Elect/2025-26
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Transformer & panels | Item1 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Supply,installation, testing and commissioning of LT distribution Transformer 2500 KVA, 11/0.433 kV oil immersed outdoor type, energy efficent (level-2) having following specifications and confirming to IS 1180 and IS 2026, complete with all accessories as reqd. | item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | Rating :2500kVA | item3 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4 | Type : Outdoor Distrubution Transformer | item4 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5 | IS Standard: IS 1180 IS 2026 (Level-2) | item5 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | Cooling Type : ONAN (oil natural and air natural) | Item6 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7 | No. of Winding : Two | Item7 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
8 | No. of phases : Three | Item8 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
9 | Voltage Ratio : 11/0.433 kV | Item9 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | Vector Group Reference : Dyn 11 | Item10 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11 | Insulation Class : F | Item11 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12 | OTI, WTI & low oil level with marshaling box with alarm and trip contacts. | Item12 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | Manual tap changer + 7.5% to - 7.5% in steps of 2.5% OCTC. | Item13 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14 | Buchholz relay with alarm and trip contacts and valve on conservator side connection. HV side cable box 2R x 3 C x 240 sq.mm. box and LV side box arrangement for 4000 A bus duct connection as reqd. complete. | Item14 | 2 | Set | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
15 | Supply installation , testing & commissioning of 4000 A FP aluminium busduct with 100 % neutral, IP 55 with 2 mm MS enclosure, including 4000 A copper flexibles connection at both ends of transfromer and LT panels. busduct both side having 2 runs of 25x5 mm GI strip for earthing connection, space heater, silica gel breather and shall be panted with black mat finish paint with MTG arrangment, spcifications confirming to IS 8623, IEC 60529 as reqd. complete. | Item15 | 30 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
16 | Supply, installation, testing and commissioning of indoor type, metal clad switchgear with fabricated from 2 mm thick CRCA/ Aluzinc material, Maximum system voltage 12 kV and rated 11 kV, 1250 amp, 25kA/1Sec VCB panel with 8 no's VCBs with integrated operating handle, totally enclosed and fully interlocked with self support copper busbar, horizontal draw out breaker with all compartments type tested for internal arc for 25 kA for 1 sec as per IS 13118, IS 12729 IEC 62271-100, as amended up to date, breakers should be interchangeable between incomers & feeders and having following specifications complete as reqd. | Item16 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
17 | Incoming (2 set, incomer-1 from 33kV ss & incomer -2 from SS 4)- 3P 1250 A VCB electrically operated, draw out type with completely encapsulated poles and continuous rated closing & tripping coils. | Item17 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Three nos 800-400/5-5 ratio, 2.5VA, class 1.0 Resin Cast Current Transformer for metering purposes and class 5P10 Resin Cast Current Transformer for protection purposes. | Item18 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19 | Three nos. Potential Transformer 11kV/110V epoxy cast resin,class I for metering and class 3P for protection withdrawable type with HT fuse | Item19 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
20 | Numerical relay with LCD Display - 3 over current + Earth Fault with instantaneous element with IDMT/ DMT characteristics selectable at site , master trip relay hand reset type trip circuit supervision function, inrush protection, record and store at least 100 Events with Date and Time Stamp, Last Five Fault Records stored in Non-volatile memory , Self Supervision function, Minimum 4 Digital Binary Inputs and 6 Digital output Contacts, Modbus communication Protocol with RS-485 Port, Breaker Control (ON/OFF) ,Modbus protocol for communication., Antipumping relay. | Item20 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
21 | Multifunction Meter with RS485 communication port scada compateble. | Item21 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | One Set of Red / Green / Indication Lamps for close and open position. One Amber indicating lamp for trip circuit healthy. One Set of white phase indication lamps for phase. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Outgoing (7 set, O/G-1 for TR-1,O/G 2 for TR-2,O/G3 for TR-1 ss9,O/G4 for TR-2 ss9,O/G5 TR-1 SS11, O/G6&7 spare) - Eight nos, 3 pole 1250A VCB electrically operated, draw out type with completely encapsulated poles, and continuous rated closing & tripping coils. | Item23 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24 | Three Nos. 300-150 /5-5 ratio, 2.5 VA, Class 1.0 Resin Cast Current Transformers for metering purposes and Class 5P10 Resin Cast Current Transformers for Protection Purposes. | Item24 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Instrument & Protection Panel - Numerical relay with LCD display- 3 OC+ 1 E/F with instetenious element IDMT/DMT characteristics selectable at site , master trip relay hand reset type trip circuit supervision function, inrush protection, record and store at least 100 Events with Date and Time Stamp, Last Five Fault Records stored in non-volatile memory, Self Supervision function, Minimum 4 Digital Binary Inputs and 6 Digital output Contacts, Modbus Communication Protocol with RS-485 Port, scada compateble remote Breaker Control (ON/OFF) feature over Modbus. | Item25 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
26 | Auxiliary relay for fault (OTI, WTI, Buchholz-Alarm and Trip | Item26 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Each feeder having Multifunction Meter with RS485 communication port, scada compateble. Elite 440 or equivalent multi -line phase digital panel meter for accurate and reliable measurement of electric parameters(V,I,W,F..etc.) for industrial and commercialapplications. Ithas a large multi line backlit display which enables four parameters to be displayed simultaneously.Modbus communication capability allows easy integration with energy monitorir system.Expansion modules can be fitted for enhane system integration(Pulse input/output or eathernet) Connection tyep:HV3/HV4/LV4 aplications, measurement Voltage:57.7/100V to 240/415V AC, Standards: IS13779,IS14697,IEC62052-11,IEC62053-21,IEC62053-23,IEC62053-22,IEC61010,IEC62053-31,Dimensions:96mmx96mmx65mm, Ingress Protection:IP-54, Load Survey: 6 parameters for 40days,at 30 minutes integration, Addiional Plug in modules: 2 pulse inputs,2pulse outputs module,4 analogue output module,Ethernet gateway module. | Item27 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28 | One Set of Red / Green / Indication Lamps for close and open position. One Amber indicating lamp for trip circuit healthy. One Set of white phase indication lamps for phase. | Item28 | 1 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Supply installation testing and commissioning of cubical type LT panel suitable for 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferable) design from CRCA sheet steel of 2mm thick for frame work and covers. 3mm thick for gland plated i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type FP Aluminium alloy 4000A Bus bars of high conductivity. DMC.SMC bus bar supports, with short circuit withstand capacity of 70 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos earth solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant low smoke insulated copper conductor s/c cable, cable alleys, cable gland plate in two half. | Item29 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
30 | The panel shall be equipped with relays, timers set of CT's for metering & protection and energy analyser to indicate current phase, line voltage, frequency, power factor, KWH, KVARH. Provision of over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications conforming to IS 8623 and IEC 60439 amended up to date complete as reqd. | Item30 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
31 | Incoming from 2500 kVA Transformer( TR-1) | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | 1 No's 4000A, FP, EDO,70 kA, ACB with micro processor based release for O/C,S/C& E/F protection with LCD display 2NO+2NC Aux. Contact. Trip contact T&C. etc. | Item32 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
33 | With ON,OFF,Trip ,RYB, indication. Digital multifunction KWH meter. Digital Amp and volt meter with selector switches etc. | Item33 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
34 | Out Going: supplying and fixing of following ACB and MCCB as outgoings in panel. | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | 2 nos.2500 A, FP, EDO, 50 kA ACB with microprocessor based O/C,S/C,& E/F protection. Safety Shutter. 2NO+2NC Aux. Contact etc. 2 Nos with T-N-C. | Item35 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | 2 nos.1600 A, FP, EDO, 50 kA ACB with microprocessor based O/C,S/C,& E/F protection. Safety Shutter. 2NO+2NC Aux. Contact etc. 2 Nos with T-N-C. | Item36 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
37 | 2 nos. 800 A, TPN, EDO, 50 kA ACB with microprocessor based O/C,S/C,& E/F protection. Safety Shutter. 2NO+2NC Aux. Contact etc. 2 Nos with T-N-C. | Item37 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
38 | 2 nos. 630 A, TPN, 50 kA,MCCB with Microprocessor based O/C,S/C,&E/F protection with rotary handle. | Item38 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
39 | 4 nos. 400 A, TPN, 50 kA,MCCB with Microprocessor based O/C,S/C,&E/protection with rotary handle. | Item39 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | 2 nos. 250 A, TPN, 50 kA,MCCB with Microprocessor based O/C,S/C,&E/F protection with rotary handle. | Item40 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
41 | 2 nos. 100 A, TPN, 50 kA,MCCB with Microprocessor based O/C,S/C,&E/F protection with rotary handle. | Item41 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
42 | all out goings with ON.OFF, indication. Digital multifunction meter . Digital Amp meter with selector switches etc. | Item42 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
43 | Each feeder having Multifunction Meter with RS485 communication port, Elite 440 or equivalent is multi -line phase didgital panel meter for accurate and reliable measurement of electric parameters(V,I,W,F..etc.) for industrial and commercialapplications. Ithas a large multi line backlit display which enables four parameters to be displayed simultaneously.Modbus communication capability allows easy integration with energy monitorir system.Expansion modules can be fitted for enhane system integration(Pulse input/output or eathernet) Connection tyep:HV3/HV4/LV4 aplications, measurement Voltage:57.7/100V to 240/415V AC, Standards: IS13779,IS14697,IEC62052-11,IEC62053-21,IEC62053-23,IEC62053-22,IEC61010,IEC62053-31,Dimensions:96mmx96mmx65mm, Ingress Protection:IP-54, Load Survey: 6 parameters for 40days,at 30 minutes integration, Addiional Plug in modules: 2 pulse inputs,2pulse outputs module,4 analogue output module,Ethernet gateway module. | Item43 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | Bus Bar | Item44 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
45 | 4000A 415V, 3 phase 4 wire busbar (100% neutral) 50Hz Aluminium bus bar | Item45 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
46 | Note : All ACBs and MCCB's aux. contacts for ON/OFF and trip spare contacts to be wired up to terminal block. | Item46 | 1 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Supply, Installation, testing and commisssioning of cubical type LT panel incoming from DG synchronizing panel & TR-2 suitable for 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferbly) design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick for gland plated i/c cleaning & finshing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type TPN Aluminium allloy Bus bars of high conductivity , DMC.SMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of size 25mm x 6mm at the rear with 2 Nos. earth stud solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant insulated copper condutor s/c cable, cable alleys, cable gland plate in two half. | Item47 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
48 | The panel shall be eqipped with relays, timers set of CTs for metering & protection and energy analyzer to indicate current phase, line voltage, frequency, power factor, KWH, KVARH, Provisionof over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications amended conforming to IS 8623 and IEC 60439 and competibility to PLC system (IEC 61131-3) amended up to date complete as reqd. | Item48 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
49 | Incoming -1 form DG Synchronized panel | Item49 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
50 | 1 No. 4000A 50 kA 4Pole EDO ACB with MP Based Release For O/C, S/C & E/F Protection, Motor 230Vac, Closing Coil 230Vac, S/T and Safety Shutter, 2NO+2NC Aux. Contact, Trip contact , T & C.etc. | Item50 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
51 | with ON,OFF,Trip ,RYB, indication, Digital KWH meter, Digital Amp and volt meter with selector switches etc. | Item51 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
52 | Incoming-2 from 2500KVA Transformer -2 | Item52 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
53 | 1 No. 4000A 50 kA 4Pole EDO ACB with MP Based Release For O/C, S/C & E/F Protection, Motor 230Vac, Closing Coil 230Vac, S/T and Safety Shutter, 2NO+2NC Aux. Contact, Trip contact , T & C. etc. | Item53 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
54 | with ON,OFF,Trip ,RYB, indication, Digital KWH meter, Digital Amp and volt meter with selector switches etc. | Item54 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
55 | with ON,OFF,Trip ,RYB, indication etc | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Out Going: supplying and fixing of following ACB and MCCB as outgoings | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | a) 2 No's 2500A 50kA 4Pole MDO ACB with MP Based Release For O/C, S/C & E/F Protection, Safety Shutter, 2NO+2NC Aux. Contact etc. with T & C. | Item57 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
58 | b) 3 No's 800A 50 kA 4Pole MDO ACB with MP Based Release For O/C, S/C & E/F Protection, Safety Shutter, 2NO+2NC Aux. Contact etc. with T & C. | Item58 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
59 | c) 3 nos. 400 A, TPN, 50 kA,MCCB with Microprocessor based O/C,S/C,&E/protection with rotary handle. | Item59 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
60 | d) 3 nos. 250 A, TPN, 50 kA,MCCB with Microprocessor based O/C,S/C,&E/F protection with rotary handle. | Item60 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | e) 3 nos. 100 A, TPN, 50 kA,MCCB with Microprocessor based O/C,S/C,&E/F protection with rotary handle. | Item61 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
62 | all out goings with ON.OFF, indication. Digital multifunction meter . Digital Amp meter with selector switches etc. | Item62 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
63 | Each feeder having Multifunction Meter with RS485 communication port, Elite 440 is multi -line phase didgital panel meter for accurate and reliable measurement of electric parameters(V,I,W,F..etc.) for industrial and commercialapplications. Ithas a large multi line backlit display which enables four parameters to be displayed simultaneously.Modbus communication capability allows easy integration with energy monitorir system.Expansion modules can be fitted for enhane system integration(Pulse input/output or eathernet) Connection tyep:HV3/HV4/LV4 aplications, measurement Voltage:57.7/100V to 240/415V AC, Standards: IS13779,IS14697,IEC62052-11,IEC62053-21,IEC62053-23,IEC62053-22,IEC61010,IEC62053-31,Dimensions:96mmx96mmx65mm, Ingress Protection:IP-54, Load Survey: 6 parameters for 40days,at 30 minutes integration, Addiional Plug in modules: 2 pulse inputs,2pulse outputs module,4 analogue output module,Ethernet gateway module complete as reqd. | Item63 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
64 | Bus Bar | Item64 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | 4000A 415V, 3 phase 4 wire busbar (100% neutral) 50Hz Aluminium bus bar | Item65 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
66 | Note : All ACBs and MCCB's aux. contacts for ON/OFF and trip spare contacts to be wired upto terminal block. | Item66 | 1 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
67 | PLC Panel (PLC based manual & Auto over-ride) | Item67 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
68 | Supply, Installation, testing and commissioning of auto main failure (AMF), auto synchronizing, auto load sharing, auto load management based on demand feedback. PLC shall collect demand feedback from MFM in ATS panels/ transformer incomers & nececcasry wiring & communication from meter to PLC, auto change over/ inter locking DG control and operation programmable logic panel cubicle type made of 2mm thick CRCA sheet enclosure, powder coated, free standing, floor mounted, dust vermin proof, indoor suitable for 3x750 KVA DG sets complete with all measuring instruments, protective devices, alarm etc. as required for above functions rated & analogue input & output modules, input/ output racks, power supplies communication with PLC with communication cables etc. as required and degree of protection IP:52 & all relays shall be microprocessor based comprising,conforming to ( IEC 61131-3) and IS 8623 and IEC 60439 as complete reqd. | Item68 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
69 | Metering/ Monitoring (Synchronizing Equipment) | Item69 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
70 | Double Voltmeter 0-500 PTR 415/110V - Analog - 1No. | Item70 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
71 | Double frequency meter PTR 415V/110V-REED - 1No. | Item71 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
72 | Dark lamp / bright lamp- 2 Nos. | Item72 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
73 | 3 Line Display Multifunction Meter - 6 Nos. | Item73 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
74 | Switch /selector/ PB | Item74 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
75 | Sychronizing Switch - 1 No. | Item75 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
76 | Set Selector Switch - 1No. | Item76 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
77 | Manual / Auto switch - 1 No. | Item77 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | Test push Button Yellow with 1 No. Contact - 1No. | Item78 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
79 | Accept Push Button Blue with 1 No. Contact - 1No. | Item79 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
80 | Reset push Button Black with 1 No. Contact - 1No. | Item80 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
81 | Engine Start Push Button Green with 2 Nos. Contact - 3 Nos. | Item81 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Engine Stop Push Green with 2 Nos. Contact - 3 Nos. | Item82 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
83 | Circuit Breaker close Push Button Green with 1 No. Contact - 4 Nos. | Item83 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
84 | Circuit Breaker Trip Push Button Red with 2 Nos. Contact - 4 Nos. | Item84 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
85 | Emergency Stop Push Button Mushroom Red with 1 No. Contact - 3 Nos. | Item85 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
86 | Voltage Raise / Lower Joysticks with 2 Nos. Contact - 3 Nos. | Item86 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
87 | Speed Raise/ Lower Joysticks with 2 Nos. Contact - 3 Nos. | Item87 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
88 | LED - 1 set | Item88 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
89 | PLC Hardware (Sychronizing Equipment) | Item89 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
90 | PLC-CPU-Battery Free CPU with on board profibus/ ethernet part - 1 No. | Item90 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | On line 2 KVA UPS for PLC & CPU for 30 minute backup | Item91 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
92 | PC based HMI (human machine interface) with core 2 Dup processor, 500 GB HDD, 2 GB RAM, DVD Writer, Optical Mouse Multimedia Key Board, 43" LED Monitor with Licensed Windows Operating System or Latest updated available hardware and software at the time of purchase. | Item92 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
93 | Digital Input Module - Minimum 16 CH per DG. | Item93 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
94 | Digital Output Module - Minimum 16 CH per DG. | Item94 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | MMC (Micro Memory Card) 128 KB - 1 No. | Item95 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
96 | Software for PLC programming (licenced) with mimic diagram - 1 Set | Item96 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
97 | Licenced software for runtime application - 1 set | Item97 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
98 | PLC Sychronisations with following annunciation/ control features - 3 sets (1 for each DG set) | Item98 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
99 | Engine Fault Relay | Item99 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
100 | LLOP ON Delay | Item100 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
101 | Fuel Solenoid Relay | Item101 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
102 | Speed Lower Relay | Item102 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Speed Raise Relay | Item103 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
104 | Voltage Lower Relay | Item104 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
105 | Voltage Raise Relay | Item105 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
106 | Under Voltage Aux. Relay | Item106 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Trip Command Relay | Item107 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
108 | DC Failure Relay | Item108 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
109 | Reverse Power Relay | Item109 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
110 | Rotor Earth Fault Relay | Item110 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
111 | Loss of Excitation Relay | Item111 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
112 | check Synchronizing Relay (Synchromax of Conzerve or equivalent) | Item112 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
113 | Pilot Lights / Indications | Item113 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
114 | Pilot Light Amber 230V AC (DC Failure) - LED type - 1 No. | Item114 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
115 | Pilot Light Red 24V AC (on) - LED type - 6 Nos. (for DG set, TR I/C & B/C) | Item115 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
116 | Pilot Light Red 24V AC (off) - LED type - 6 Nos. (for DG set, TR I/C & B/C) | Item116 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
117 | Annunciator 12 channel for - 24V DC - 1 No. for synchronizing | Item117 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
118 | Power Supply | Item118 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | 230V AC / 24V DC, 10A, Stablises power Supplies with voltage trimmer - 1 set | Item119 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | Maintenance Free Batter 12 V, 40AH - 2 Nos. | Item120 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
121 | Micellaneous Components | Item121 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
122 | Exhaust fan - 6" - 2 Nos. | Item122 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
123 | Control MCB - 1 Set | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Panel Light - 11W CFL - 2 Nos. | Item124 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
125 | Door Switch - 6A - 2 Nos. | Item125 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
126 | Space Heater - 65W - 1 No. | Item126 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
127 | Switch Socket - 5A / 15A, 6 pin - 1 No. | Item127 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
128 | Solid State Alarm 24V DC - 1 No. | Item128 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
129 | Terminals - 2.5 sqmm - 1 set | Item129 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
130 | Panel + Hardware | Item130 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
131 | Earth Bus - Copper - set | Item131 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
132 | Earth Links for Door Earthing | Item132 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | Enclosure - 1 Set | Item133 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
134 | Filters - 1 Set | Item134 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
135 | Terminal Mounting Track - 1 Set | Item135 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
136 | Terminal Anchor End - 1 Set | Item136 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
137 | DG/ Bus monitoring PT's - 1 Set | Item137 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
138 | Suitable for 3 no's Incomer form (DG-1,DG-2,DG-3), 3 no's 1600A 50 kA 4Pole EDO ACB with MP Based Release For O/C, S/C & E/F Protection, Motor 230Vac, Closing Coil 230Vac, S/T and Safety Shutter, 2NO+2NC Aux. Contact, Trip contact etc. | Item138 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
139 | Out going 4000A 50 kA 4Pole EDO ACB with MP Based Release For O/C, S/C & E/F Protection, Motor 230Vac, Closing Coil 230Vac, S/T and Safety Shutter, 2NO+2NC Aux. Contact, Trip contact etc | Item139 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Suitable for Bus Bar 4000A/50 kA, 3 Ph, 4-wire, 50Hz, 4P Aluminium Busbar with Colour Coded Heat Shrinkable sleeves | Item140 | 1 | Set | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
141 | Supply installation testing and commissioning of cubical type DG synchronising panel (PLC based synchronising panel i.e through item no.5) for 3 x 750 KVA DG sets.suitable for 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferable) design from CRCA sheet steel of 2mm thick for frame work and covers. 3mm thick for gland plated i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type FP Aluminium alloy Bus bars of high conductivity. DMC.SMC bus bar supports, with short circuit withstand capacity of 70 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos earth solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant low smoke insulated copper conductor s/c cable, cable alleys, cable gland plate in two half. | Item141 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
142 | The panel shall be equipped with relays, timers set of CT's for metering & protection and energy analyser to indicate current phase, line voltage, frequency, power factor, KWH, KVARH. Provision of over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications amended up to date complete. and attached specification conforming to IS 8623 and IEC 60439 complete as reqd. | Item142 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
143 | 3 no's Incomer form DG-1,DG-2,DG-3, 1600A 50 kA 3 Pole EDO ACB & Neutral contactor with MP Based Release For O/C, S/C & E/F Protection, Motor 230Vac, Closing Coil 230Vac, S/T and Safety Shutter, 2NO+2NC Aux. Contact, Trip contact etc. | Item143 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
144 | 4000A,50 kA, 3 Ph, 4-wire, 50Hz, 4P Aluminium Busbar with Colour Coded Heat Shrinkable sleeves | Item144 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Out going 4000A 50kA 4Pole EDO ACB with MP Based Release For O/C, S/C & E/F Protection, Motor 230Vac, Closing Coil 230Vac, S/T and Safety Shutter, 2NO+2NC Aux. Contact, Trip contact etc. | Item145 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
146 | DG Synchroning through PLC panel (Auto/Mannual) | Item146 | 1 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
147 | APFC & AHF panel | Item147 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
148 | Supplying , installation , testing and commissioning of 2 mm thick CRCA sheet cubical type floor mounted Activecomp - Hybrid series Hybrid Harmonic Filter and power mangement System panel (Capacitor Banks & Active Harmonic Filters) . as per specifications conforming to IS 16636 and IESC 61921 and IEC 61439 comlete as reqd. | Item148 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
149 | Controller | Item149 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
150 | 3 Phase 3 CT Controller with inbuit load and Harmonic Analyser | Item150 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
151 | Modular Active Filter Unit | Item151 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
152 | IGBT Fired Modular (for Harmonic Mitigation) | Item152 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
153 | Switching | Item153 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
154 | SCR-SCR Type Solid State,trasnsient free switching module for capacitor Reactor Filter Banks | Item154 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
155 | Inductors | Item155 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
156 | Class - H insulation and exceptionally low temperature rise | Item156 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
157 | Capacitors | Item157 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | Low loss DUCA power super Heavy Duty type in a 3 phase cylindrical aluminium case | Item158 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
159 | IGBT Fired Modular Active Filter Units | Item159 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
160 | Thyristor/Contactor Switched Tunde / Detuned Filter Units | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Touch Screen Display Unit for AHF | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | High Filtration Efficiency | Item162 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
163 | Hybrid Technology | Item163 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
164 | Low Operational Cost | Item164 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
165 | Long Operational Life | Item165 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
166 | IGBT Fired Modular Active Filter Units | Item166 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
167 | Thyristor/Contactor Switched Tunde / Detuned Filter Units | Item167 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
168 | Touch Screen Display Unit for AHF | Item168 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
169 | High Filtration Efficiency | Item169 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Hybrid Technology | Item170 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
171 | Low Operational Cost | Item171 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
172 | Long Operational Life | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | Enclosure Design: standardized bolted Modular Sheet Steel Eclosure - Non Compartmentalized | Item173 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
174 | Enclosure Finish: Epoxy Poweder Coated, in grey (RAL 7035) Structure finish | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | Rated Design Voltage: 415V -440V, 50Hz,3 phase 3 wire | Item175 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
176 | Output Rating: 600 KVAR | Item176 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
177 | Duty: Continuous | Item177 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
178 | Capacitors: DUCA POWER Super Heavy Duty series | Item178 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
179 | Reactors : H-Class,Single layer Wound 200% Linearity, Al, high RMS current capability | Item179 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
180 | Switching:Heavy Duty Thyristor Switched,SCR-SCR type for 415V network | Item180 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
181 | Active Harmonic Filter:IGBT Fired modular AHF unit | Item181 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Display:Touch Screen/ Graphic Display with Power Quality Parameters | Item182 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
183 | Incoming: 3 pole ACB | Item183 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
184 | Outgoing:MCCB | Item184 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
185 | Ambient Temperature: 50° C max short time, 40° C average in 24 Hrs, 35° annual average. -10° C low limit | Item185 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
186 | Protection Class: IP 42 | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Instruments & Indications: Real time power factor comtroller with Dual P.F Control & capable to show lag lead Kvah,display waveforms,RS-485,HMI unit for Modular AHF Units, SMPS supply,protection n each relay output,Auo manual selector switch | Item187 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
188 | Bus Bars: 0.8Amp Per Sq.mm, FP,Electrolytic grade AL. bus bar | Item188 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
189 | Capacity : 600 KVAR | Item189 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
190 | Incomer : ACB 1250 A, 3 P, 50 kA with microprocessor based O/C,S/C protection. | Item190 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
191 | Out Goings for Banks: | Item191 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
192 | For 2 No. 25 KVAR : MCCB 63 A, 3 P, 36 kA with adjustable O/L, S/C, release & ROH and 63 A TP capacitor duty contactor with 2NO+2NC. | Item192 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
193 | For 3 no's 50 KVAR : MCCB 125 A, 3 P, 36 kA with adjustable O/L, S/C, release & ROH and 110 A TP capacitor duty contactor with 2NO+2NC. | Item193 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
194 | For 4 no's 100 KVAR : MCCB 250 A, 3 P, 36 kA with adjustable O/L, S/C, release & ROH and 250 A TP capacitor duty contactor with 2NO+2NC. | Item194 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
195 | Banks: 2No's 25 kVAR, 3 No.s 50 kVAR, ,4 Nos. 100 kVAR with APP heavy duty Capacitors and seven percent copper wound reactors. | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | APFC Relay : 12 stage | Item196 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
197 | Outgoings (Active Filter Section) (i) 630A TP MCCB,36 kA with O/L & S/C protection, On OFF,Trip Indication. (ii) 400A Actiive filter 3P 4W with suitable rating of Modules in IP-30 emclosure with provision of adding 125A future each module should have individual protection. | Item197 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
198 | Metering: Digital Volt and Amp meter, exhaust fan, LED type indicating lamp, controlling system etc.Each feeder having Multifunction Meter with RS485 communication port, Elite 440 is multi -line phase didgital panel meter for accurate and reliable measurement of electric parameters(V,I,W,F..etc.) for industrial and commercialapplications. Ithas a large multi line backlit display which enables four parameters to be displayed simultaneously.Modbus communication capability allows easy integration with energy monitorir system.Expansion modules can be fitted for enhane system integration(Pulse input/output or eathernet) Connection tyep:HV3/HV4/LV4 aplications, measurement Voltage:57.7/100V to 240/415V AC, Standards: IS13779,IS14697,IEC62052-11,IEC62053-21,IEC62053-23,IEC62053-22,IEC61010,IEC62053-31,Dimensions:96mmx96mmx65mm, Ingress Protection:IP-54, Load Survey: 6 parameters for 40days,at 30 minutes integration, Addiional Plug in modules: 2 pulse inputs,2pulse outputs module,4 analogue output module,Ethernet gateway modu | Item198 | 2 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
199 | Earthing | Item199 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
200 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Item200 | 20 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
201 | Supplying & fixing 50mm x 6mm thick GI earth strip in ground / surface or in recess for connection etc. as reqd. | Item201 | 500 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
202 | Providing and fixing earth bus of 50 mm X 5 mm copper strip on surface for connections etc. as required. | Item202 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Item203 | 8 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | Item204 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
205 | HT & LT cable | Item205 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
206 | Supply of one no. 3 core 240sq.mm A2XFY, XLPE insulated PVC sheathed 11kV (E) /6.6 kV(UE) grade XLPE HT power cables (heavy Duty) aluminium conductor,steel armoured cable, as per IS 7098 part-2 complete as required. | Item206 | 4500 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
207 | Supply of one no. 3 core 95sq.mm A2XFY,XLPE insulated,PVC sheathed 11kV (E) /6.6 kV (UE) grade XLPE HT power cables (heavy Duty) aluminium conductor,steel armoured cable as per IS 7098 part-2 complete as required. | Item207 | 300 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11kV (E) /6.6 kV(UE) grade of following size direct in ground including excavation, sand cushioning,protective covering and refilling the trench etc as required. | Item208 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
209 | upto 120 sq. mm | Item209 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
210 | Above 120 sq. mm and upto 400 sq. mm | Item210 | 1210 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
211 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 11 kV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required | Item211 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
212 | upto 120 sq. mm | Item212 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
213 | Above 120 sq. mm and upto 400 sq. mm | Item213 | 2270 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
214 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11kV grade of following size in the existing RCC/ HUME/ METAL pipe as required. | Item214 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
215 | upto 120 sq. mm | Item215 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
216 | Above 120 sq. mm and upto 400 sq. mm | Item216 | 665 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
217 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11kV grade of following size in the existing masonry open duct as required. | Item217 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
218 | upto 120 sq. mm | Item218 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
219 | Above 120 sq. mm and upto 400 sq. mm | Item219 | 355 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
220 | Supplying of one No. 3½C x 400 sq.mm. A2XFY, XLPE insulated steel armoured aluminium conductor power cable of grade 1.1 kV PVC sheathed power cables (heavy duty) confirming to IS 7098 (Part-1) aluminium conductor, steel armoured cable as reqd complete in following manners. | Item220 | 5000 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
221 | Supplying of one No. 3½C x 240 sq.mm. A2XFY, XLPE insulated steel armoured aluminium conductor power cable of grade 1.1 kV PVC sheathed power cables (heavy duty) confirming to IS:7098 (Part-1) aluminium conductor, steel armoured cable as reqd complete in following manners. | Item221 | 200 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
222 | Supplying of one No. 3½C x 95sq.mm. A2XFY, XLPE insulated steel armoured aluminium conductor power cable of grade 1.1 kV PVC sheathed power cables (heavy duty) confirming to IS:7098 (Part-1) aluminium conductor, steel armoured cable as reqd complete in following manners. | Item222 | 300 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
223 | Supplying of one No. 3½C x 35sq.mm. XLPE steel armoured aluminium conductor power cable of grade 1.1 kV PVC sheathed power cables (heavy duty) confirming to IS:1554(Part-1) 1988/7098 (Part-1) aluminium conductor, steel armoured cable as reqd complete in following manners. | Item223 | 200 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
224 | Supplying of one No. 2C x 10sq.mm. A2XFY, XLPE insulated steel armoured aluminium conductor power cable of grade 1.1 kV PVC sheathed power cables (heavy duty) confirming to IS: 7098 (Part-1) aluminium conductor, steel armoured cable as reqd complete in following manners. | Item224 | 250 | Mtr | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
225 | Supply of the 7 core x 2.5 sq.mm control cable of 1.1Kv grade armoured XLPE insulated sheathed copper Conductor as per IS 7098 part-1. | Item225 | 250 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
226 | Laying of one no. number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size direct in ground i/c excavation, sand cushioning, protective covering and refilling the trench etc as reqd. | Item226 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
227 | Upto 35 sq. mm | Item227 | 275 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
228 | Above 35 sq. mm and upto 95 sq. mm Metre | Item228 | 120 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
229 | Above 185 sq. mm and upto 400 sq. mm | Item229 | 2175 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
230 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required | Item230 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
231 | Upto 35 sq. mm | Item231 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
232 | Above 35 sq. mm and upto 95 sq. mm Metre | Item232 | 45 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
233 | Above 185 sq. mm and upto 400 sq. mm | Item233 | 2000 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
234 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL pipe as required | Item234 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
235 | Upto 35 sq. mm | Item235 | 130 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
236 | Above 35 sq. mm and upto 95 sq. mm Metre | Item236 | 45 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
237 | Above 185 sq. mm and upto 400 sq. mm | Item237 | 500 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
238 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing masonry open duct as required | Item238 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
239 | Upto 35 sq. mm | Item239 | 95 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
240 | Above 35 sq. mm and upto 95 sq. mm Metre | Item240 | 45 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
241 | Above 185 sq. mm and upto 400 sq. mm | Item241 | 500 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
242 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size on wall surface as required | Item242 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
243 | Upto 35 sq. mm | Item243 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
244 | Above 35 sq. mm and upto 95 sq. mm Metre | Item244 | 45 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
245 | Above 185 sq. mm and upto 400 sq. mm | Item245 | 25 | Mtr | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
246 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc. as required. | Item246 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
247 | 150 mm dia | Item247 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
248 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc. as required | Item248 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
249 | 50 mm Dia | Item249 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
250 | 80 mm Dia | Item250 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
251 | 100 mm Dia | Item251 | 1200 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
252 | Supplying and laying Insulating mat "Shock safe" in front of electrical panels, complete as requied rubber mat of standard size 3.0 mm thick for up to 22 kV class B confirming to IS 15652 as required complete. | Item252 | 30 | Sq. Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
253 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 kV grade as required | Item253 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
254 | 95 Sq.mm | Item254 | 12 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
255 | 240 sq.mm. | Item255 | 18 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
256 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable/control cable of 1.1kV grade as required. | Item256 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
257 | 2 x 10 Sq.mm (with Aluminium Lugs) | Item257 | 25 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
258 | 3½ C x 35 sq.mm. (with Aluminium Lugs) | Item258 | 6 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
259 | 3½ C x 95 sq.mm. (with Aluminium Lugs) | Item259 | 6 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
260 | 3½ C x 240 sq.mm. (with Aluminium Lugs) | Item260 | 6 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
261 | 3½ C x 400 sq.mm. (with aluminium Lugs) | Item261 | 60 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
262 | 7 C x 2.5 sqmm (with copper Lugs) | Item262 | 20 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
263 | Digging trench for taking out cable and refilling , watering ,ramming the sameafter taking out cable as reqd complete.cable size up to 400Sq.mm | Item263 | 300 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
264 | Lifting removing cable up to 400 sq.mm. size from trench/clamps, making role & depositing the same in departmental store I/c cartage. | Item264 | 300 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
265 | Dismentling of brass compression type gland up to 400 sq. mm. Cable | Item265 | 15 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
266 | Supplying and fixing carbon diaoxide ( CO2) type fire extingushers confirming to IS 2878:1976 and cylinder fully charged of following capacity. | Item266 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
267 | 4.5 Kg. fire extinguisher wall mounted | Item267 | 30 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
268 | 9 Kg. fire extinguisher trolly mounted | Item268 | 30 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
269 | Supply,fixing of 4 no's FIRE bucket 9.5 liters capacity GI bucket i/c filling sand, painted in post office red clour with prior coat of red oxide paint and writte with white paint 'FIRE' and mounted on MS angle iron frame with bracket with 35 x 35x 5 mm size angle in required shape,1.5mm MS sheet shed covered i/c cutting, welding, as standard specified suitable for Electrical substations & as directed by EIC. | Item269 | 5 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
270 | Fixtures & fittings | Item270 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
271 | Supplying and fixing exhaust fan 450 mm sweep (18") with louvers/ shutter in existing opening including connections, testing & commissioning etc. as reqd. | Item271 | 3 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
272 | Supply and fixing of 1 X 20W LED fitting, IP20 , 2000 lumen output, 6500k, aluminium housing, polycarbonate cover, surface mounted, 140V-270V operating Volt. etc. complete with all fixing accessories as required complete. | Item272 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
273 | Supply and installation testing and commissioning of 36W LED 2'x2' fittings surface mounted, IP20, 3300 Lumens colour temperature 6500 K, with metallic CRCA powder coated housing cover high efficiency diffuser, THD less than10, power factor above 0.9. | Item273 | 60 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
274 | Supply and fixing testing and commissioning of 40 Watt garden light/ postop lanterndecorative post top for 360 degree indirect light with IP65 protection resistance to impact and corrosion Gkare free and better uiniformity with high power LEDs, luminaires on the existing pole as required complete. | Item274 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
275 | Supply and installation testing and commissioning of 18W LED round and square surface mounted LED panel PDC alluminium housing and high transiucent, IP20, 2000 Lumens colour temperature 6500 K, with metallic CRCA powder coated housing cover high efficiency diffuser, THD less than10, power factor above 0.9 complete as required. | Item275 | 20 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
276 | S/F testing commissioning of street light Luminures. Endura sundown 45W LED , die-cast aluminium IP66,make:havells or its equvalent, on the existing street light pole complete as required. | Item276 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
277 | Supplying and fixing of 32 mm dia X 2.00 metres long G.I. pipe (medium class) bracket for mounting of fluorescent / HPMV / HPSV street light fitting on pole including bending the pipe to the required shape, 2 nos 40 mm X 3 mm flat iron clamps with nuts, bolts and washer, painting the flat iron with primer and finish paint etc. as required. | Item277 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
278 | Supply, installation testing and commissioning of 5 star rating ceiling fan 1200mm sweep, 320 rpm, 230 CMM air delivery full copper wound motor, white powder coated, without regulator with down rod of standard length (up to 30cm) with 1.5 sqmm PVC copper single core wire. etc as required complete. | Item278 | 40 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
279 | Numbering of ceiling fan/exhaust fan / street light poles fitting/ as reqd. | Item279 | 150 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
280 | S&F extra down rod of 10 cm length seam less conduit pipe, 15 mm dia heavy gauge, I/c painting etc. as reqd. (Note: More than 5cm length shall be rounded off to the nearest 10 cm and 5 cm or less shall be ignored). | Item280 | 25 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
281 | Supply & fixing of 65 mm dia.'B' class GI pole 4.5 mtr. Long for post top lantern i/c bas plate 300 x 300 x 3mm GI reducer & nipple for mounting the fitting with painting etc. grouting in cement concrete 1: 3: 6 (1 cement : 3 coarse sand : 6 grade stone aggregate 40mm complete as reqd. | Item281 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
282 | Internal wiring | Item282 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
283 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and Earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required. | Item283 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
284 | Group B | Item284 | 70 | Points | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
285 | Group C | Item285 | 70 | Points | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
286 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface/recessed steel conduit,2 way modular type switch, modular plate, suitable GI box and Earthing the point with 1.5sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. | Item286 | 5 | Points | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
287 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and Earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. | Item287 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
288 | Group B | Item288 | 50 | Points | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
289 | Group C | Item289 | 50 | Points | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
290 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLSH PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required | Item290 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
291 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | Item291 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
292 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Item292 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
293 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | Item293 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
294 | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | Item294 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
295 | 4 X 10 sq. mm + 2 X 6 sq. mm earth wire | Item295 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
296 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel / PVC conduit as required. | Item296 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
297 | 1x 1.5 sqmm | Item297 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
298 | 4 x 1.5 sqmm | Item298 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
299 | 4 x 4.0 sqmm | Item299 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
300 | 6 x 6 sq. mm | Item300 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
301 | Supplying and drawing of following sizes of FRLSH PVC insulated copper conductor, 3 core round cable of following size in the existing surface/ recessed steel/ PVC conduit as required. | Item301 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
302 | 1.5 sq. mm | Item302 | 100 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
303 | S & F 40 amp to 63 amp rating 240 volts 'C' curve 10 kA MCB of following pole in the existing MCB DB complete with connection, testing & commissioning etc as reqd. ( legrand) | Item303 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
304 | Triple Pole | Item304 | 4 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
305 | Four Pole | Item305 | 2 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
306 | Providing and fixing circular/ Hexagonal cast iron or M.S. sheet box for ceiling fan clamp, of internal dia 140 mm, 73 mm height, top lid of 1.5 mm thick M.S. sheet with its top surface hacked for proper bonding, top lid shall be screwed into the cast iron/ M.S. sheet box by means of 3.3 mm dia round headed screws, one lock at the corners. Clamp shall be made of 12 mm dia M.S. bar bent to shape as per standard drawing. | Item306 | 40 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
307 | Supplying and fixing of following sizes of steel conduit along with accessories in surface / recess including painting in case of surface conduct, or cutting the wall and making good the same in case of recessed conduit as required. | Item307 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
308 | 20mm dia 16 SWG | Item308 | 100 | Mtr | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
309 | 25mm dia 16 SWG | Item309 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
310 | 32 mm dia 16 SWG | Item310 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
311 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. | Item311 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
312 | 3 Module (100mmX75mm) | Item312 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
313 | 6 Module (200mmX75mm) | Item313 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
314 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as reqd. | Item314 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
315 | 180 x 100 x 60 mm deep | Item315 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
316 | 200 x 250 x 75 mm deep | Item316 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
317 | 250 x 300 x 100mm deep | Item317 | 10 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
318 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required | Item318 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
319 | 5/6 amp switch | Item319 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
320 | 15/16 amp switch | Item320 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
321 | 3 pin 5/6 amp socket outlet | Item321 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
322 | 6 pin 15/16 Amp. Socket outlet | Item322 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
323 | Telephone socket outlet | Item323 | 5 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
324 | stepped type fan regulator | Item324 | 40 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
325 | modular blanking plate | Item325 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
326 | Supplying and fixing 3 pin, 5 amp. ceiling rose on the existing junction box/wooden block I/c connection etc. as reqd. | Item326 | 50 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
327 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | Item327 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
328 | Single Pole | Item328 | 72 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
329 | Single Pole & Neutral | Item329 | 8 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
330 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FRLS PVC insulated copper conductor up to the terminal connector/ neutral link, Earthing etc. as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) | Item330 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
331 | 12 way double door (4+36) | Item331 | 2 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
332 | Providing & fixing MV danger notice plate of 200mm x 150mm make of mild steel at least 2mm thick vitreous enamelled white on both sides and with inscriptions in signal red colours in front side as reqd. | Item332 | 4 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
333 | Providing & fixing HT danger notice plate of 250mm x 200mm make of mild steel at least 2mm thick vitreous enamelled white on both sides and with inscriptions in signal red colours in front side as reqd. | Item333 | 4 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
334 | Supplying and laying chequered plate in cut pcs of 6mm thick with handle cutting/ welding as required complete. | Item334 | 50 | Sq. Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
335 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete up to plinth level. Cold twisted bars | Item335 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
336 | Cold twisted bars | Item336 | 100 | Kg. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
337 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : | Item337 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
338 | 1:3:6 (1 Cement : 3 coarse sand (zone-III) derived from natural nsources : 6 graded stone aggregate 40 mm nominal size derived from natural sources) | Item338 | 5 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
339 | Brick work with common burnt clay F.P.S (non modular) bricks of class designation 7.5 in foundation and plinth in; | Item339 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
340 | cement mortar 1:4 (1 cement : 4 coarse sand) | Item340 | 5 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
341 | 15 mm thick cement plaster on the rough side of single or half wall of mix; | Item341 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
342 | 1:4 (1 cement : 4 fine sand) | Item342 | 10 | Sq.mtr. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
343 | Supplying and fixing 'C' Channel of size 100 x 50 mm ISMC in cut sizes i/c cutting/ welding as required complete. | Item343 | 70 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
344 | Excavation for foundation in soft soil including dressing of sides and ramming of bottoms, lift up to 1.5 m including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres. | Item344 | 10 | cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
345 | Supplying and laying of 32mm (8Kg / cm²) HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984, Part II complete with fitting and cutting, jointing etc. in the existing open duct, complete as required. | Item345 | 200 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
346 | Supplying and laying of 63mm (8Kg / cm²) HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984, Part II complete with fitting and cutting, jointing etc. in the existing open duct, complete as required. | Item346 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
347 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | Item347 | 200 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
348 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | Item348 | 50 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
349 | Providing and fixing double scaffolding system (cup lock type) on the exterior side, up to seven story height made with 40 mm dia M.S. tube 1.5 m centre to centre, horizontal & vertical tubes joining with cup & lock system with M.S. tubes, M.S. tube challies, M.S. clamps and M.S. staircase system in the scaffolding for working platform etc. and maintaining it in a serviceable condition for the required duration as approved and removing it there after .The scaffolding system shall be stiffened with bracings, runners, connection with the building etc wherever required for inspection of work at required locations with essential safety features for the workmen etc. complete as per directions and approval of Engineer-in-charge .The elevational area of the scaffolding shall be measured for payment purpose .The payment will be made once irrespective of duration of scaffolding. | Item349 | 200 | Sqmtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
350 | Supplying and drawing of UTP 4 pair CAT 6 LAN cable in the existing surface/recessed steel/PVC conduit as required. | Item350 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
351 | 1 run of cable | Item351 | 250 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
352 | 2 run of cable | Item352 | 250 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
353 | Drawing of optical cable enhanced CAT6 cable in existing steel conduit pipe/GI pipe/raceway/RCC pipe as required. The cost shall also include numbering of networking wire from room to rack as required (Cat 6 cable supplied by the department) | Item353 | 250 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
354 | Fixing of RJ-45 modular box with cover plate or I/o box for internet on surface/ recessed cutting the wall making good the same as required. ( box and cover plate will be supplied by dept.) | Item354 | 10 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
355 | Providing and fixing following rating and breaking capacity and pole MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. | Item355 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
356 | 125 A,16KA,TP MCCB | Item356 | 2 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
357 | Supplying and fixing of light class G.I. pipe of 50 mm dia. (nominal) 3 metres length along the pole for protection of under ground cable as required. | Item357 | 3 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
358 | S&F, connecting and commissioning looping type cable end control box with 2mm fabricated CRCA sheet of size 200 mm x 200 mm x 125 mm having 1 no. 6amp to 32 amp SPMCB 250 volt and 2 nos. brass neutral link square rod 6 way and fixed on 3mm thick bakelite sheet. Box shall have almirah type hing and panel key type lock front door duly painted with earthing strud etc. complete as required | Item358 | 10 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
359 | Supply & fixing shock treatment chart duly mounted on a wooden frame with 5mm thick glass approximate frontara 1.20 sq.meter. | Item359 | 5 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
360 | Supply & fixing safety instruction chart duly mounted on a wooden frame with 5mm thick glass approximate frontara 1.20 sq.meter. | Item360 | 5 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
361 | Supply & fixing of 35x35x5mm or higher size angle iorn in required shape and size including cutting,welding,painting complete required as directed by the Engineer Incharge | Item361 | 50 | Kg | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information